## Instructions
NPS Project Sustainability Checklist - Instructions
National Park Service (NPS) - Denver Service Center (DSC) ¦ 4-5-23
Building and Non-Building Projects for New Construction or Renovation
1 | Acronyms and abbreviations used in this checklist are listed below.
2 | This checklist accounts for progress in meeting federal and sustainability requirements (Guiding Principles).
3 | Complete the Project Information, Predesign (PD), and Schematic Design (SD) worksheets. On the PD and SD worksheets, respond with Y (Yes), N (No), or N/A (Not Applicable) for each sustainability feature. Where applicable: complete cells highlighted in yellow; select appropriate options by placing X in the cell to the left of the option; and include a concise explanation of how the requirement is or is not met. The purpose of this checklist, first and foremost, is to record whether sustainability features are included. Therefore, it is not sufficient to indicate a feature is not in the (design or construction) contract. The response should indicate whether this project includes the feature at the particular deliverable stage, and if so, how. Example:
4 | All federal requirements must be met for all new buildings and major building renovations. For building renovation projects costing less than 50% of the current replacement value of the building, the project must only comply with federal requirements applicable to the planned work.
5 | Complying with all 6 Guiding Principles is required for a building to be considered in compliance. Projects meeting certification requirements of LEED (Leadership in Energy & Environmental Design) at any of the four levels may not necessarily be compliant with the Guiding Principles.
6 | For non-building projects, use this same checklist. For federal requirements that do not apply to this non-building project, indicate with N/A. Non-building projects are defined as construction projects that do not include the construction of a building. Examples may include trailside parking, utility line, and road projects. For projects seeking formal or informal LEED certification, submit a USGBC LEED scorecard.
7 | Sustainability requirements from 2020 Guiding Principles for Sustainable Federal Buildings are indicated with green.
8 | Federal Building Performance Standards (BPS) 2022 requires at least 30% of federal buildings, measured by GSF, to achieve zero scope 1 emissions from on-site fossil fuel use through building electrification.
Acronyms & Abbreviations used in this Checklist:
A/E | Architect/Engineer
AC/H | Air Changes per Hour
ABS | Acrylonitrile Butadiene Styrene
AEDG | Advanced Energy Design Guides
ASHRAE | American Society of Heating, Refrigeration, and Air Conditioning Engineers
BDR | Basis of Design Report
BPS | Building Performance Standards
CD | Construction Documents
CFC | Chlorofluorocarbon
cfm/sf | cubic feet per minute per square foot
CFR | Code of Federal Regulations
Ci/L | Picocurie per Liter
CPVC | Chlorinated Polyvinyl Chloride
CRV | Current Replacement Value
CSA | Canadian Standards Association
DSC | Denver Service Center
EA | Energy & Atmosphere (LEED)
EISA | Energy Independence and Security Act
EO | Executive Order
EPA | Environmental Protection Agency
EPACT | Energy Policy Act
EPEAT | Electronic Product Environmental Assessment Tool
ETS | Environmental Tobacco Smoke
FEMP | Federal Energy Management Program
FMSS | Facility Management Software System
FSC | Forest Stewardship Council
FY | Fiscal Year
GS | Green Seal
GSF | Gross Square Feet
HCFC | Hydrofluorocarbon
HVAC | Heating, Ventilating and Air Conditioning
IAQ | Indoor Air Quality
IECC | International Energy Conservation Code
LEED | Leadership in Energy and Environmental Design
MERV | Minimum Efficiency Reporting Value
N/A | Not Applicable
NC | New Construction (LEED)
NPS | National Park Service
PD | Predesign
PMIS | Project Management Information System
PVC | Polyvinyl Chloride
RCRA | Resource Conservation and Recovery Act
RH | Relative Humidity
SCAQMD | South Coast Air Quality Management District
SD | Schematic Design
SFI | Sustainable Forestry Initiative
SWPPP | Storm Water Pollution Prevention Plan
USDA | United States Department of Agriculture
USGBC | United States Green Building Council
VCT | Vinyl Composition Tile
VOC | Volatile Organic Compound
WBDG | Whole Building Design Guide

## Project Information
NPS Project Sustainability Checklist - Building and Non-Building Projects for New Construction or Renovation - Project Information
Project Title: |  | Project Type:
Description: |  | Gross Building Construction Cost:
A/E Firm: |  | Gross Non-Building (e.g. Site) Cost:
Building Size (Square Feet):
| Park: | Type of Building:
| PMIS Number: | If Renovation, Existing Building CRV:
FMSS Number:
| Date: | Program Funding Source:
Year Predesign Began:
| LEED Certification Level (if applicable): | Fiscal Year of Construction Funding:
| Formal or Informal: | State of Project Location or N/A (if project is not in a state):
*For new buildings 5,000 GSF or more and major renovations to buildings greater than or equal to 5,000 GSF, contract with an |  | If it can be shown that meeting the 30% performance standard for new construction (or 20% for
independent Commissioning Authority and comply with ASHRAE 0-2005, "The Commissioning Process". |  | major renovations) is not life-cycle cost effective over 40 years, then the project must incorporate
the maximum energy savings that can be shown to be life-cycle cost effective.
For smaller projects, comply with requirements of LEED NC 2009, EA Prerequisite 1, "Fundamental Commissioning of the
Building Energy Systems" (which allows the commissioning authority to be an employee of the design firm). |  | For new building projects with a lower net construction value, an alternative method is to meet or
exceed the minimum requirements prescribed by ASHRAE AEDG (a much simpler prescriptive
**For new building projects of 5,000 GSF or more, perform whole building energy simulation(s) in accordance with ASHRAE 90.1 |  | method for achieving the target) to be life-cycle cost effective.
(or IECC residential) to show performance at least 30% better (20% for major renovations) than a code compliant similar building.
For buildings without an appropriate AEDG, perform whole building energy simulation(s) in
By FY 2030, at least 30% of federal buildings, measured by GSF, achieve zero scope 1 emissions from on-site fossil fuel use |  | accordance with ASHRAE 90.1 (or IECC residential).
through building electrification. (Federal BPS 2022)

## Predesign (PD)
Predesign (PD) |  | Project Title: | 0
Yes, No, N/A | Sustainability Feature | X | Concisely explain how all requirements are met at this milestone.
SITES
| Construction Activity Pollution Prevention |  | Erosion and Sediment Control Strategies
Develop a Storm Water Pollution Prevention Plan (SWPPP).
| Stormwater Discharges from Construction Activities |  | Temporary seeding/planting
Permanent seeding/planting
Mulching
Earth dike
Silt fence
Sediment trap
Sediment basin
Other:
| Stormwater Management |  | Protect Hydrology
For development footprints that exceed 5000 square feet, maintain or restore, to the maximum extent
| 1.3 Stormwater Management | technically feasible, the predevelopment hydrology of the property with regard to the temperature, rate,
| (Guiding Principles for Sustainable Federal Buildings 2020) | volume, and duration of flow.
Vegetated roofs
| Stormwater Management for Federal Facilities |  | Pervious paving
| (EISA Section 438) |  | Reuse stormwater for landscape irrigation.
Reuse stormwater for toilet and urinal flushing.
Reuse stormwater for custodial uses.
Grid pavers
Rain gardens
Vegetated swales
Constructed wetlands
Vegetated filters
If project involves no site work, answer Yes.
Other:
| Soundscape Preservation |  | Soundscape Preservation
No exterior noise producing equipment.
| 4.9 Soundscape Management |  | Exterior noise producing equipment is quieter than ambient noise levels.
| (2006 NPS Management Policies) |  | Sound screening is installed to reduce noise levels of outside noise producing equipment.
Other:
| Dark Sky Preservation |  | Dark Sky Preservation
Minimize site lighting.
| 4.10 Lightscape Management |  | All exterior features are full cutoff luminaries.
| (2006 NPS Management Policies) |  | Exterior surfaces are low-reflectance.
Spotlights are low-angle.
If no exterior lighting on site/building, answer yes.
If existing building has existing non-cutoff lighting that will remain, answer No.
Other:
WATER EFFICIENCY
| Water Meters |  | Water Metering
A new water meter will be provided.
| 3.2 Water Metering |  | Building has an existing water meter.
| (Guiding Principles for Sustainable Federal Buildings 2020) |  | For irrigation systems larger than 25,000 square feet, a separate water meter will be provided.
Other:
NPS Metering of Water and Energy Use - New Construction
| HVAC Water Efficiency |  | Water Used for Energy Conservation
For such systems, ensure life-cycle cost-effective water conservation technologies are applied.
| Section 109 Federal Building Performance Standards | Systems that use water for energy conservation:
| (EPA of 2005) |  | Evaporative cooling
Cooling tower
Domestic water heat rejection loop
Other:
| Indoor Water Use |  | Water Metering
Employ strategies that minimize water use and waste:
| 3.1 Indoor Water Use |  | Select plumbing fixtures that are WaterSense labeled and comply with ASHRAE 189.1-2014.
| (Guiding Principles for Sustainable Federal Buildings 2020) |  | Water bottle filling station integrated into drinking fountain units.
FEMP designated products.
Cooling tower controls optimized.
Eliminate single pass cooling systems.
| Outdoor Water Use |  | Protect and Conserve Water
Employ strategies that minimize water use and waste:
| 3.3 Outdoor Water Use |  | Water efficient landscaping using native, non-invasive, low maintenance plant species.
| (Guiding Principles for Sustainable Federal Buildings 2020) |  | 50% water use reduction using ASHRAE 189.1-2014 methodologies.
Do not irrigate beyond the establishment of plantings.
| Alternative Water Use |  | Protect and Conserve Water
Employ strategies that minimize water use and waste:
| 3.4 Alternative Water |  | Capture rainwater.
| (Guiding Principles for Sustainable Federal Buildings 2020) |  | Treated wastewater.
Use of grey water.
Use of reclaimed water.
Other:
ENERGY / ENVIRONMENT
| Fundamental Commissioning |  | Fundamental Commissioning
Systems/tests that may be included:
| 1.5 Commissioning |  | HVAC systems (mechanical and passive) and associated controls
| (Guiding Principles for Sustainable Federal Buildings 2020) |  | Lighting and day lighting controls
Domestic hot water systems
| Meet Performance Objectives |  | Renewable energy systems (wind, solar, etc.)
| (WBDG) |  | Building envelope
Blower door testing
| 3. The Federal Building Peformance Standard |  | Other:
(Federal BPS 2022)
Deliverables for this requirement include:
Owner's project requirements
Basis of Design Report (BDR)
Commissioning plan
Incorporate commissioning requirements into Construction Documents (CD).
Functional performance testing
Commissioning report
|  | . | NPS recommends performing blower door testing on applicable projects to determine overall
tightness of building envelope.
|  | . | Blower door test should be performed with a pressure differential between indoors and outdoors of
50 Pascals.
|  | . | Resulting building tightness should be 3 to 5 air changes per hour (AC/H). (Curatorial storage
buildings should be 1 AC/H at 50 Pascals.)
|  | . | If building falls outside this range, make improvements to building envelope and retest until within
recommended range.
|  | . | Infrared thermography could be used in conjunction with blower door testing to identify areas of
air leakage and building components that are significant sources of heat loss/heat gain.
| Enhanced Commissioning |  | Enhanced Commissioning
| (Required for large or complex buildings or systems.) | Systems/tests may be included under Fundamental Commissioning:
HVAC Systems (Mechanical & Passive) and associated controls
| 1.5 Commissioning |  | Lighting and day lighting controls
| (Guiding Principles for Sustainable Federal Buildings 2020) |  | Domestic hot water systems
Renewable energy systems (wind, solar, etc.)
| 3. The Federal Building Peformance Standard |  | Building envelope
| (Federal BPS 2022) |  | Blower door testing
Other:
One acceptable standard for commissioning is ASHRAE 0-2005.
Deliverables for commissioning include:
Owner's project requirements
Basis of Design Report (BDR)
Commissioning plan
Conduct commissioning design review prior to mid-Construction Documents.
Incorporate commissioning requirements into Construction Documents.
Review construction submittals.
Functional performance testing
Verify training requirements are complete.
Review building operation within 10 months after substantial completion.
Commissioning report
Commissioning process began during design.
|  | . | NPS recommends performing blower door testing on applicable projects to determine overall
tightness of building envelope.
|  | . | Blower door test should be performed with a pressure differential between indoors and outdoors of
50 Pascals.
|  | . | Resulting building tightness should be 3 to 5 Air Changes per Hour (AC/H). (Curatorial storage
buildings should be 1 AC/H at 50 Pascals).
|  | . | If building falls outside of this range, make improvements to building envelope and re-test until within
recommended range.
|  | . | Infrared thermography could be used in conjunction with blower door testing to identify areas of air
leakage and building components that are significant sources of heat loss/heat gain.
| Refrigerant Management |  | Zero Use of Ozone Depleting Compounds (Chlorofluorocarbon (CFC) and Hydrofluorocarbon (HCFC)
Zero use of CFC based refrigerants in HVAC and refrigerant systems.
| 5.4 Ozone Depleting Substances |  | If existing HVAC systems are used, a CFC phase out conversion will occur prior to project
| (Guiding Principles for Sustainable Federal Buildings 2020) |  | completion. Refrigerant will be recovered and recycled.
Examples of refrigerants with zero ozone depleting potential: HFC-23, 134a, 245fa, 404A, 407C,
410A, 507A
| Energy Performance |  | Demonstrate a percent improvement over ASHRAE 90.1
New buildings:
| Part 433 - Energy Efficiency Standards for the Design and Construction of new |  | 12%
| Federal Commercial and Multi-Family High-Rise Residential Buildings |  | 14%
| (10 CFR - Energy) |  | 16%
18%
| 2.1 Energy Efficiency |  | 20%
| (Guiding Principles for Sustainable Federal Buildings 2020) |  | 22%
24%
| Optimize Energy Performance.** |  | 26%
| (Federal Regulations require an energy consumption reduction of 30% for New Construction |  | 28%
| and 20% for Existing Building Renovation as compared to an ASHRAE 90.1 baseline.) |  | 30% (Federal Requirement)*
32%
| 3. The Federal Building Peformance Standard |  | 34%
| (Federal BPS 2022) |  | 36%
38%
40%
42%
46%
48%
Other: %
Existing buildings:
8%
10%
12%
14%
16%
18%
20% (Federal Requirement)*
22%
24%
26%
28%
30%
32%
34%
36%
38%
40%
42%
44%
Other: %
Federal Energy performance is based on compliance with ASHRAE 90.1 current version.
| Reduce Fossil Fuel Derived Energy |  | Demonstrate Reduction in Fossil Fuel Derived Energy (For new construction and major renovations greater than $2,500,000.)
80% reduction by 2020
| Section 433 Federal Building Energy Efficiency Performance Standards |  | 95% reduction by 2025
| EISA 2007 |  | 100% reduction by 2030
Other:
| 3. The Federal Building Peformance Standard | Fossil fuel derived energy should be reduced compared to a similar building from fiscal year 2003
| (Federal BPS 2022) | as measured by the Commercial Buildings Energy Consumption Survey.
| Procure Environmentally Sustainable Electronic Products |  | Energy Efficient Electronic Products
| (Predominantly relates to purchases of desktop/laptop computer and peripherals.) | Electronic Product Environmental Assessment Tool (EPEAT) Products:
Desktop computers
| EO 14057 Catalyzing Clean Energy Industries and Jobs Through Federal Sustainability |  | Laptop computers
Computer workstations
| 2.1 Energy Efficiency |  | Computer monitors
| (Guiding Principles for Sustainable Federal Buildings 2020) |  | Other:
| Energy Star and Federal Energy Management Program (FEMP) |  | Energy Star or FEMP Designated Products
Lighting
| Section 436.4 Purpose and Scope |  | Commercial HVAC equipment and motors
| (CFR - Title 10 Energy - Part 436 Federal Energy Management and Planning Programs - |  | Food service equipment
| Subpart C Agency Procurement of Energy Efficient Products) |  | Office equipment
Home electronics
| Federal Procurement Policies for ENERGY STAR Certified Products |  | Appliances
Residential HVAC equipment and motors
| 3. The Federal Building Peformance Standard |  | Plumbing equipment
| (Federal BPS 2022) |  | Building envelope components
Water Sense labeled products
Energy Star or FEMP designated products - not available.
Energy Star and FEMP designated projects - not cost effective over life of product.
Energy Star and FEMP designated projects - do not meet functional requirements of project.
Other:
| Premium Efficiency Electric Motors |  | Premium Efficiency Motors
Provided on all motors greater than or equal to 1.0 horse power.
| Section 104 Procurement of Energy Efficiency Products |  | Other:
| (EPA of 2005) | This includes motors specified under both Mechanical and Electrical Divisions.
| On-Site Renewable Energy*** |  | Solar Thermal
| Solar Thermal for Hot Water |  | Drain Back solar water heating system
| (Choose N/A if proven not life cycle cost effective.) |  | Thermosiphon solar water heating system
Direct circulation system
| Section 523 - Standard Relating to Solar Hot Water Heaters |  | Indirect water heating system
| (EISA of 2007) |  | Solar thermal is not life cycle cost effective over 40 years.
3. The Federal Building Peformance Standard
(Federal BPS 2022)
Other:
| Metering - Measurement and Verification |  | Building Meters
Natural gas
| 2.2 Energy Metering |  | Steam
| (Guiding Principles for Sustainable Federal Buildings 2020) |  | Electric
Other:
EO 14057 Catalyzing Clean Energy Industries and Jobs Through Federal Sustainability
3.6 Federal BPS Performance Management and Reporting
(Federal BPS 2022)
MATERIALS AND RESOURCES
| Storage and Collection of Recyclables |  | Recyclables - Storage & Collection
Designate an area for recyclable collection and storage appropriately sized and located in
| 5.6 Solid Waste Management |  | convenient area.
| (Guiding Principles for Sustainable Federal Buildings 2020) |  | Identify local waste handlers and buyers for glass, plastic, metals, office paper, newspaper,
and organic wastes.
Instruct occupants on recycling procedures.
Install cardboard balers.
Install aluminum can crushers.
Install recycling chutes.
Other:
| Construction Waste Management |  | Construction Waste Management - Divert Minimum 50% from Disposal
% diversion rate:
| 5.6 Solid Waste Management |  | Develop waste management plan.
| (Guiding Principles for Sustainable Federal Buildings 2020) |  | Identify materials to be recycled.
Establish if measure will be weight or volume.
Establish if materials will be sorted on site or comingled.
Other:
| Recycled Content |  | Regional Materials
Onsite salvaged materials
| 5.1 Materials - Recycled Content |  | Regionally obtained concrete
| (Guiding Principles for Sustainable Federal Buildings 2020) |  | Regionally obtained lumber
Regionally obtained plant based materials
| RCRA Section 6002 Solid Waste Disposal Act |  | Other:
(Products that meet or exceed / recycled content recommendations.)
EO 14057 Catalyzing Clean Energy Industries and Jobs Through Federal Sustainability
| Bio-Based Products |  | BioPreferred Products
BioPreferred form release agent
| EO 14057 Catalyzing Clean Energy Industries and Jobs Through Federal Sustainability |  | BioPreferred carpet
BioPreferred sealants and coatings
| USDA BioPreferred |  | Other:
| Certified Wood |  | Certified Wood*
Certified wood for permanent installation
| Identifying Greener Wood Products |  | Certified wood for temporary use (forms, bracing, scaffolding, etc.)
Other:
*Suggested wood certifications include Forest Stewardship Council (FSC), Sustainable Forestry
Initiative (SFI), and Canadian Standards Association (CSA).
INDOOR ENVIRONMENTAL QUALITY
| Indoor Air Quality (IAQ) |  | Minimum IAQ
Meet the requirements of ASHRAE 62.1-2007.
| 4. Enhance the Indoor Environment |  | Other:
(Guiding Principles for Sustainable Federal Buildings 2020)
| Environmental Tobacco Smoke (ETS) Control |  | Environmental Tobacco Smoke Control
Smoking will be prohibited in the building and anywhere within 25 feet of entries, outdoor air
| 4.7 Environmental Smoking Control |  | intakes, and operable windows.
| (Guiding Principles for Sustainable Federal Buildings 2020) |  | Signage is provided to allow smoking in designated areas, prohibit smoking in other areas,
or prohibit smoking on entire property.
Other:
| IAQ Management Plan - During Construction |  | Construction IAQ Management Plan - During Construction
Prepare IAQ management plan.
| 4.6 Indoor Air Quality during Construction and Operations |  | Do not use permanent HVAC systems during demolition and/or construction.
| (Guiding Principles for Sustainable Federal Buildings 2020) |  | Protect equipment from dust and odors and seal all duct and equipment openings with plastic.
If permanent systems will be used during demolition and/or construction, install and maintain
filters (Minimum Efficiency Reporting Value (MERV) 8 minimum) on all returns.
If permanent systems will be used during demolition and/or construction and an unducted
plenum over the construction zone must be used, all ceiling tiles will be in place.
All filtration media shall be replaced after construction and before occupancy.
Construction activities shall be isolated to prevent contamination of clean or occupied spaces.
Cleaning activities to control contaminants in building.
Other:
| IAQ Management Plan - Before Occupancy |  | Construction IAQ Management Plan - Before Occupancy
Prepare IAQ management plan.
| 4.9 Occupant Health and Wellness |  | Perform building flushout (14,000 cubic foot per square feet of building) with air 60 degrees
| (Guiding Principles for Sustainable Federal Buildings 2020) |  | Fahrenheit or higher and less than 60% RH (relative humidity).
Perform flushout (3500 cubic feet per square foot of building) and after occupancy, provide a
minimum 0.30 cubic feet per minute per square foot (cfm/sf) outside air or as determined by
ASHRAE 62.1-2007, whichever is greater, until a total of 14,000 cubic feet per square foot of
building has been delivered to the space.
Conduct baseline IAQ testing, after construction and before occupancy, in accordance with
"Environmental Protection Agency (EPA) Compendium of Methods for the Determination of Air
Pollutants in Indoor Air".
Other:
| Low-Emitting Materials - Adhesives and Sealants |  | Low Emitting Adhesives and Sealants
Use low-emitting (low or no volatile organic compound (VOC)) materials on at least 75% of interior
| 4.3 Low-Emitting Materials and Products | products by cost or surface area.
| (Guiding Principles for Sustainable Federal Buildings 2020) |  | Low VOC carpet adhesive
Low VOC carpet pad adhesive
Low VOC wood flooring adhesive
Low VOC rubber floor adhesive
Low VOC subfloor adhesive
Low VOC ceramic tile adhesive
Low VOC vinyl composition tile (VCT) and asphalt adhesive
Low VOC drywall and panel adhesive
Low VOC cove base adhesive
Low VOC multipurpose construction adhesive
Low VOC structural glazing adhesive
Low VOC polyvinyl chloride (PVC) glue
Low VOC chlorinated polyvinyl chloride (CPVC) glue
Low VOC acrylonitrile butadiene styrene (ABS) glue
Low VOC plastic welding
Low VOC plastic primer
Low VOC contact adhesive
Low VOC structural wood member adhesive
Low VOC sheet applied rubber lining
Low VOC top and trim adhesive
Low VOC architectural sealant
Low VOC nonmembrane roof sealant
Low VOC roadway sealant
Low VOC single ply roof membrane sealant
Low VOC sealant primer, architectural nonporous
Low VOC sealant primer, architectural porous
Low VOC metal to metal adhesive
Low VOC plastic foam adhesive
Low VOC porous material (except wood) adhesive
Low VOC wood adhesive
Low VOC fiberglass adhesive
Other:
| Low-Emitting Materials - Paints and Coatings |  | Low Emitting Paints & Coatings
Use low-emitting (low or no volatile organic compound (VOC)) materials on at least 75% of interior
| 4.3 Low-Emitting Materials and Products | products by cost or surface area.
| (Guiding Principles for Sustainable Federal Buildings 2020) |  | Low VOC bond breakers
Low VOC varnish
Low VOC lacquer
Low VOC concrete curing compounds
Low VOC dry-fog coatings
Low VOC fire-retardant coatings
Low VOC flat paints
Low VOC floor coatings
Low VOC nonflat high gloss coatings
Low VOC nonflat non-high gloss coatings
Low VOC quick dry enamels
Low VOC shellac
Low VOC stains
Paints are Green Seal (GS) Standard GS-11 compliant.
Clear wood finishes are South Coast Air Quality Management District (SCAQMD) Rule 113 compliant.
All anti-corrosive and anti-rust paints are GS Standard GC-03 compliant.
Other:
| Low-Emitting Materials - Flooring Materials |  | Low Emitting Flooring Systems
Carpet meets testing and product requirements of Carpet and Rug Institute Green Label Plus Program.
| 4. Enhance the Indoor Environment |  | All carpet cushion meet requirements of Carpet and Rug Institute Green Label Program.
| (Guiding Principles for Sustainable Federal Buildings 2020) |  | Hard surface flooring must be compliant with FloorScore.
Other:
| Moisture Control |  | Moisture Control
Building envelope assemblies conform to recommended practices on
| 4.5 Moisture and Mold Control |  | DSC Workflows Design Standards > Architectural Standards
| (Guiding Principles for Sustainable Federal Buildings 2020) |  | Building envelope assemblies conform to moisture control. (See ASHRAE Fundamentals 2021.)
Building envelope assemblies conform to Moisture Control Handbook (Lstiburek and Carmody 1991)
| EO 14057 Catalyzing Clean Energy Industries and Jobs Through Federal Sustainability |  | for recommended practices.
Other:
| Controllability of Systems - Lighting |  | Controllability of Lighting
Individual lighting control for building occupants.
| 4. Enhance the Indoor Environment |  | Separate lighting controls for shared multi-occupant spaces to meet group needs.
| (Guiding Principles for Sustainable Federal Buildings 2020) |  | Other:
| Thermal Comfort Design |  | Thermal Comfort Design
Building meets requirements of ASHRAE 55-2020.
| 4.1 Ventilation and Thermal Comfort |  | Other:
(Guiding Principles for Sustainable Federal Buildings 2020)
| Daylighting and Lighting Controls |  | Daylight
Provide daylight control for interior lighting.
| 4.2 Daylight and Lighting Controls |  | Install interior light shelf to project daylighting further into spaces.
| (Guiding Principles for Sustainable Federal Buildings 2020) |  | Install exterior light shelf for glare control.
Install fixed exterior shading devices for glare control.
Provide windows in occupied spaces for occupants to obtain daylight.
Provide skylights in occupied spaces for occupants to obtain daylight.
Task lighting
Other:
| Radon |  | Radon
New Construction - Incorporate radon resistant construction techniques.
| Radon-Resistant Construction Basics and Techniques |  | Install course gravel layer, perforated pipe, or collection mat below foundation.
Install heavy duty plastic sheeting or vapor retarder over gravel layer.
| 4.4 Radon Mitigation |  | Install vent pipe vertically from gravel to roof.
| (Guiding Principles for Sustainable Federal Buildings 2020) |  | Seal all openings and cracks in concrete foundations and walls with polyurethane caulk.
Install electrical J-Box (Junction-Box) for use with a vent fan.
Major Renovations
Test for radon prior to construction.
For levels greater than or equal to 4pCi/L (Picocurie per Liter), employ radon mitigation techniques.
| Integrated Pest Management |  | Integrated Pest Management
Potential pest species have been discussed with NPS and building design incorporates strategies
| NPS Integrated Pest Management Program |  | to manage identified pests.
Other:
4.8 Integrated Pest Management
(Guiding Principles for Sustainable Federal Buildings 2020)
| Occupant Health and Wellness |  | Occupant Health and Wellness
Building or site-wide health and fitness programs
| WBDG Promote Health and Well-Being |  | Fitness center
Convenient access to healthy dining options
| 4.9 Occupant Health and Wellness |  | Active/ergonomic work stations
| (Guiding Principles for Sustainable Federal Buildings 2020) |  | Bicycle commuter facilities
Water bottle filling stations
Access to daylight
Indoor plants
Exterior views
Other:
ADDITIONAL FEDERAL DESIGN IMPERATIVES
| Complete Integrated Design Narrative (Predesign only) |  | Integrated Design Narrative
Prepare Integrated Design Narrative.
| 1. Employ Integrated Design Principles |  | Build building at sustainable location.
| (Guiding Principles for Sustainable Federal Buildings 2020) |  | Use sustainable landscape design principles.
Other:
EO 14057 Catalyzing Clean Energy Industries and Jobs Through Federal Sustainability
| Risk Assessment |  | Risk Assessment
This building does not include critical infrastructure.
| 6.1 Risk Assessment |  | This building does include critical infrastructure.
| (Guiding Principles for Sustainable Federal Buildings 2020) |  | Use sustainable landscape design principles.
| Flood Plain Considerations |  | Flood Plain
| For mission critical buildings, adjust base flood elevation by 3 feet. For non-mission | Provide explanations:
| critical buildings, adjust base flood elevation by 2 feet. | 1
2
| 6.2 Building Resilience and Adaptation | 3
| (Guiding Principles for Sustainable Federal Buildings 2020) | 4
5
| EO 13690 - Establishing a Federal Flood Risk Management Standard and a Process for | 6
| Further Soliciting and Considering Stakeholder Input | 7
| Facility Design / Natural Hazards |  | Facility Design / Natural Hazards
| Incorporate resilience measures to mitigate the impacts of climate change and | Perform hazard assessment. Hazards identified for this project:
| natural hazards as identified on the Natural Hazards Checklist. |  | Earthquake
Landslide/Avalanche
| Natural Hazard Checklist |  | Permafrost
| (Begins on page 6 of Addressing Climate Change and Natural Hazards Handbook) |  | Cave/Karst
Shrink/Swell Soils
| 6.2 Building Resilience and Adaptation |  | Coastal Storm Surge
| (Guiding Principles for Sustainable Federal Buildings 2020) |  | Tsunami
Riverine Flood
Flash Flood
Hurricane
Tornado
Wildfire
Volcanic Eruption
Hydro-Thermal Activity (e.g. geysers)
Pest Infestation
Hazards do not occur due to geological setting.
Other:
| Facility Adaptation |  | Facility Adaptation
| For existing buildings, undergo modernization and take action to mitigate identified | Provide explanations:
| physical risks. See Natural Hazards Checklist. | 1
2
| National Hazard Checklist | 3
| (Begins on page 6 of Addressing Climate Change and Natural Hazards Handbook) | 4
5
| 6.2 Building Resilience and Adaptation | 6
(Guiding Principles for Sustainable Federal Buildings 2020)
TOP 5 SUSTAINABILITY FEATURES
| Top 5 Sustainability Features |  | Project's Top 5 Sustainable Design Features
| List the project's top 5 sustainable design features. | 1
2
3
4
5
SUSTAINABILITY SCOPE
Notes: Enter any additional details regarding the project's sustainability scope.

## Schematic Design (SD)
Schematic Design (SD) |  | Project Title: | 0
Yes, No, N/A | Sustainability Feature | X | Concisely explain how all requirements are met at this milestone.
SITES
| Construction Activity Pollution Prevention |  | Erosion and Sediment Control Strategies
Develop a Storm Water Pollution Prevention Plan (SWPPP).
| Stormwater Discharges from Construction Activities |  | Temporary seeding/planting
Permanent seeding/planting
Mulching
Earth dike
Silt fence
Sediment trap
Sediment basin
Other:
| Stormwater Management |  | Protect Hydrology
For development footprints that exceed 5000 square feet, maintain or restore, to the maximum extent
| 1.3 Stormwater Management | technically feasible, the predevelopment hydrology of the property with regard to the temperature, rate,
| (Guiding Principles for Sustainable Federal Buildings 2020) | volume, and duration of flow.
Vegetated roofs
| Stormwater Management for Federal Facilities |  | Pervious paving
| (EISA Section 438) |  | Reuse stormwater for landscape irrigation.
Reuse stormwater for toilet and urinal flushing.
Reuse stormwater for custodial uses.
Grid pavers
Rain gardens
Vegetated swales
Constructed wetlands
Vegetated filters
If project involves no site work, answer Yes.
Other:
| Soundscape Preservation |  | Soundscape Preservation
No exterior noise producing equipment.
| 4.9 Soundscape Management |  | Exterior noise producing equipment is quieter than ambient noise levels.
| (2006 NPS Management Policies) |  | Sound screening is installed to reduce noise levels of outside noise producing equipment.
Other:
| Dark Sky Preservation |  | Dark Sky Preservation
Minimize site lighting.
| 4.10 Lightscape Management |  | All exterior features are full cutoff luminaries.
| (2006 NPS Management Policies) |  | Exterior surfaces are low-reflectance.
Spotlights are low-angle.
If no exterior lighting on site/building, answer yes.
If existing building has existing non-cutoff lighting that will remain, answer No.
Other:
WATER EFFICIENCY
| Water Meters |  | Water Metering
A new water meter will be provided.
| 3.2 Water Metering |  | Building has an existing water meter.
| (Guiding Principles for Sustainable Federal Buildings 2020) |  | For irrigation systems larger than 25,000 square feet, a separate water meter will be provided.
Other:
NPS Metering of Water and Energy Use - New Construction
| HVAC Water Efficiency |  | Water Used for Energy Conservation
For such systems, ensure life-cycle cost-effective water conservation technologies are applied.
| Section 109 Federal Building Performance Standards | Systems that use water for energy conservation:
| (EPA of 2005) |  | Evaporative cooling
Cooling tower
Domestic water heat rejection loop
Other:
| Indoor Water Use |  | Water Metering
Employ strategies that minimize water use and waste:
| 3.1 Indoor Water Use |  | Select plumbing fixtures that are WaterSense labeled and comply with ASHRAE 189.1-2014.
| (Guiding Principles for Sustainable Federal Buildings 2020) |  | Water bottle filling station integrated into drinking fountain units.
FEMP designated products.
Cooling tower controls optimized.
Eliminate single pass cooling systems.
| Outdoor Water Use |  | Protect and Conserve Water
Employ strategies that minimize water use and waste:
| 3.3 Outdoor Water Use |  | Water efficient landscaping using native, non-invasive, low maintenance plant species.
| (Guiding Principles for Sustainable Federal Buildings 2020) |  | 50% water use reduction using ASHRAE 189.1-2014 methodologies.
Do not irrigate beyond the establishment of plantings.
| Alternative Water Use |  | Protect and Conserve Water
Employ strategies that minimize water use and waste:
| 3.4 Alternative Water |  | Capture rainwater.
| (Guiding Principles for Sustainable Federal Buildings 2020) |  | Treated wastewater.
Use of grey water.
Use of reclaimed water.
Other:
ENERGY / ENVIRONMENT
| Fundamental Commissioning |  | Fundamental Commissioning
Systems/tests that may be included:
| 1.5 Commissioning |  | HVAC systems (mechanical and passive) and associated controls
| (Guiding Principles for Sustainable Federal Buildings 2020) |  | Lighting and day lighting controls
Domestic hot water systems
| Meet Performance Objectives |  | Renewable energy systems (wind, solar, etc.)
| (Whole Building Design Guide (WBDG) |  | Building envelope
Blower door testing
| 3. The Federal Building Peformance Standard |  | Other:
(Federal BPS 2022)
Deliverables for this requirement include:
Owner's project requirements
Basis of Design Report (BDR)
Commissioning plan
Incorporate commissioning requirements into Construction Documents (CD).
Functional performance testing
Commissioning report
|  | . | NPS recommends performing blower door testing on applicable projects to determine overall
tightness of building envelope.
|  | . | Blower door test should be performed with a pressure differential between indoors and outdoors of
50 Pascals.
|  | . | Resulting building tightness should be 3 to 5 air changes per hour (AC/H). (Curatorial storage
buildings should be 1 AC/H at 50 Pascals.)
|  | . | If building falls outside this range, make improvements to building envelope and retest until within
recommended range.
|  | . | Infrared thermography could be used in conjunction with blower door testing to identify areas of
air leakage and building components that are significant sources of heat loss/heat gain.
| Enhanced Commissioning |  | Enhanced Commissioning
| (Required for large or complex buildings or systems.) | Systems/tests may be included under Fundamental Commissioning:
HVAC Systems (Mechanical & Passive) and associated controls
| 1.5 Commissioning |  | Lighting and day lighting controls
| (Guiding Principles for Sustainable Federal Buildings 2020) |  | Domestic hot water systems
Renewable energy systems (wind, solar, etc.)
| 3. The Federal Building Peformance Standard |  | Building envelope
| (Federal BPS 2022) |  | Blower door testing
Other:
One acceptable standard for commissioning is ASHRAE 0-2005.
Deliverables for commissioning include:
Owner's project requirements
Basis of Design Report (BDR)
Commissioning plan
Conduct commissioning design review prior to mid-Construction Documents.
Incorporate commissioning requirements into Construction Documents.
Review construction submittals.
Functional performance testing
Verify training requirements are complete.
Review building operation within 10 months after substantial completion.
Commissioning report
Commissioning process began during design.
|  | . | NPS recommends performing blower door testing on applicable projects to determine overall
tightness of building envelope.
|  | . | Blower door test should be performed with a pressure differential between indoors and outdoors of
50 Pascals.
|  | . | Resulting building tightness should be 3 to 5 Air Changes per Hour (AC/H). (Curatorial storage
buildings should be 1 AC/H at 50 Pascals).
|  | . | If building falls outside of this range, make improvements to building envelope and re-test until within
recommended range.
|  | . | Infrared thermography could be used in conjunction with blower door testing to identify areas of air
leakage and building components that are significant sources of heat loss/heat gain.
| Refrigerant Management |  | Zero Use of Ozone Depleting Compounds (Chlorofluorocarbon (CFC) and Hydrofluorocarbon (HCFC)
Zero use of CFC based refrigerants in HVAC and refrigerant systems.
| 5.4 Ozone Depleting Substances |  | If existing HVAC systems are used, a CFC phase out conversion will occur prior to project
| (Guiding Principles for Sustainable Federal Buildings 2020) |  | completion. Refrigerant will be recovered and recycled.
Examples of refrigerants with zero ozone depleting potential: HFC-23, 134a, 245fa, 404A, 407C,
410A, 507A
| Energy Performance |  | Demonstrate a percent improvement over ASHRAE 90.1
New buildings:
| Part 433 - Energy Efficiency Standards for the Design and Construction of new |  | 12%
| Federal Commercial and Multi-Family High-Rise Residential Buildings |  | 14%
| (10 CFR - Energy) |  | 16%
18%
| 2.1 Energy Efficiency |  | 20%
| (Guiding Principles for Sustainable Federal Buildings 2020) |  | 22%
24%
| Optimize Energy Performance.** |  | 26%
| (Federal Regulations require an energy consumption reduction of 30% for New Construction |  | 28%
| and 20% for Existing Building Renovation as compared to an ASHRAE 90.1 baseline.) |  | 30% (Federal Requirement)*
32%
| 3. The Federal Building Peformance Standard |  | 34%
| (Federal BPS 2022) |  | 36%
38%
40%
42%
46%
48%
Other: %
Existing buildings:
8%
10%
12%
14%
16%
18%
20% (Federal Requirement)*
22%
24%
26%
28%
30%
32%
34%
36%
38%
40%
42%
44%
Other: %
Federal Energy performance is based on compliance with ASHRAE 90.1 current version.
| Reduce Fossil Fuel Derived Energy |  | Demonstrate Reduction in Fossil Fuel Derived Energy (For new construction and major renovations greater than $2,500,000.)
80% reduction by 2020
| Section 433 Federal Building Energy Efficiency Performance Standards |  | 95% reduction by 2025
| EISA 2007 |  | 100% reduction by 2030
Other:
| 3. The Federal Building Peformance Standard | Fossil fuel derived energy should be reduced compared to a similar building from fiscal year 2003
| (Federal BPS 2022) | as measured by the Commercial Buildings Energy Consumption Survey.
| Procure Environmentally Sustainable Electronic Products |  | Energy Efficient Electronic Products
| (Predominantly relates to purchases of desktop/laptop computer and peripherals.) | Electronic Product Environmental Assessment Tool (EPEAT) Products:
Desktop computers
| EO 14057 Catalyzing Clean Energy Industries and Jobs Through Federal Sustainability |  | Laptop computers
Computer workstations
| 2.1 Energy Efficiency |  | Computer monitors
| (Guiding Principles for Sustainable Federal Buildings 2020) |  | Other:
| Energy Star and Federal Energy Management Program (FEMP) |  | Energy Star or FEMP Designated Products
Lighting
| Section 436.4 Purpose and Scope |  | Commercial HVAC equipment and motors
| (CFR - Title 10 Energy - Part 436 Federal Energy Management and Planning Programs - |  | Food service equipment
| Subpart C Agency Procurement of Energy Efficient Products) |  | Office equipment
Home electronics
| Federal Procurement Policies for ENERGY STAR Certified Products |  | Appliances
Residential HVAC equipment and motors
| 3. The Federal Building Peformance Standard |  | Plumbing equipment
| (Federal BPS 2022) |  | Building envelope components
Water Sense labeled products
Energy Star or FEMP designated products - not available.
Energy Star and FEMP designated projects - not cost effective over life of product.
Energy Star and FEMP designated projects - do not meet functional requirements of project.
Other:
| Premium Efficiency Electric Motors |  | Premium Efficiency Motors
Provided on all motors greater than or equal to 1.0 horse power.
| Section 104 Procurement of Energy Efficiency Products |  | Other:
| (EPA of 2005) | This includes motors specified under both Mechanical and Electrical Divisions.
| On-Site Renewable Energy*** |  | Solar Thermal
| Solar Thermal for Hot Water |  | Drain Back solar water heating system
| (Choose N/A if proven not life cycle cost effective.) |  | Thermosiphon solar water heating system
Direct circulation system
| Section 523 - Standard Relating to Solar Hot Water Heaters |  | Indirect water heating system
| (EISA of 2007) |  | Solar thermal is not life cycle cost effective over 40 years.
3. The Federal Building Peformance Standard
(Federal BPS 2022)
Other:
| Metering - Measurement and Verification |  | Building Meters
Natural gas
| 2.2 Energy Metering |  | Steam
| (Guiding Principles for Sustainable Federal Buildings 2020) |  | Electric
Other:
EO 14057 Catalyzing Clean Energy Industries and Jobs Through Federal Sustainability
3.6 Federal BPS Performance Management and Reporting
(Federal BPS 2022)
MATERIALS AND RESOURCES
| Storage and Collection of Recyclables |  | Recyclables - Storage & Collection
Designate an area for recyclable collection and storage appropriately sized and located in
| 5.6 Solid Waste Management |  | convenient area.
| (Guiding Principles for Sustainable Federal Buildings 2020) |  | Identify local waste handlers and buyers for glass, plastic, metals, office paper, newspaper,
and organic wastes.
Instruct occupants on recycling procedures.
Install cardboard balers.
Install aluminum can crushers.
Install recycling chutes.
Other:
| Construction Waste Management |  | Construction Waste Management - Divert Minimum 50% from Disposal
% diversion rate:
| 5.6 Solid Waste Management |  | Develop waste management plan.
| (Guiding Principles for Sustainable Federal Buildings 2020) |  | Identify materials to be recycled.
Establish if measure will be weight or volume.
Establish if materials will be sorted on site or comingled.
Other:
| Recycled Content |  | Regional Materials
Onsite salvaged materials
| 5.1 Materials - Recycled Content |  | Regionally obtained concrete
| (Guiding Principles for Sustainable Federal Buildings 2020) |  | Regionally obtained lumber
Regionally obtained plant based materials
| RCRA Section 6002 Solid Waste Disposal Act |  | Other:
(Products that meet or exceed / recycled content recommendations.)
EO 14057 Catalyzing Clean Energy Industries and Jobs Through Federal Sustainability
| Bio-Based Products |  | BioPreferred Products
BioPreferred form release agent
| EO 14057 Catalyzing Clean Energy Industries and Jobs Through Federal Sustainability |  | BioPreferred carpet
BioPreferred sealants and coatings
| USDA BioPreferred |  | Other:
| Certified Wood |  | Certified Wood*
Certified wood for permanent installation
| Identifying Greener Wood Products |  | Certified wood for temporary use (forms, bracing, scaffolding, etc.)
Other:
*Suggested wood certifications include Forest Stewardship Council (FSC), Sustainable Forestry
Initiative (SFI), and Canadian Standards Association (CSA).
INDOOR ENVIRONMENTAL QUALITY
| Indoor Air Quality (IAQ) |  | Minimum IAQ
Meet the requirements of ASHRAE 62.1-2007.
| 4. Enhance the Indoor Environment |  | Other:
(Guiding Principles for Sustainable Federal Buildings 2020)
| Environmental Tobacco Smoke (ETS) Control |  | Environmental Tobacco Smoke Control
Smoking will be prohibited in the building and anywhere within 25 feet of entries, outdoor air
| 4.7 Environmental Smoking Control |  | intakes, and operable windows.
| (Guiding Principles for Sustainable Federal Buildings 2020) |  | Signage is provided to allow smoking in designated areas, prohibit smoking in other areas,
or prohibit smoking on entire property.
Other:
| IAQ Management Plan - During Construction |  | Construction IAQ Management Plan - During Construction
Prepare IAQ management plan.
| 4.6 Indoor Air Quality during Construction and Operations |  | Do not use permanent HVAC systems during demolition and/or construction.
| (Guiding Principles for Sustainable Federal Buildings 2020) |  | Protect equipment from dust and odors and seal all duct and equipment openings with plastic.
If permanent systems will be used during demolition and/or construction, install and maintain
filters (Minimum Efficiency Reporting Value (MERV) 8 minimum) on all returns.
If permanent systems will be used during demolition and/or construction and an unducted
plenum over the construction zone must be used, all ceiling tiles will be in place.
All filtration media shall be replaced after construction and before occupancy.
Construction activities shall be isolated to prevent contamination of clean or occupied spaces.
Cleaning activities to control contaminants in building.
Other:
| IAQ Management Plan - Before Occupancy |  | Construction IAQ Management Plan - Before Occupancy
Prepare IAQ management plan.
| 4.9 Occupant Health and Wellness |  | Perform building flushout (14,000 cubic foot per square feet of building) with air 60 degrees
| (Guiding Principles for Sustainable Federal Buildings 2020) |  | Fahrenheit or higher and less than 60% RH (relative humidity).
Perform flushout (3500 cubic feet per square foot of building) and after occupancy, provide a
minimum 0.30 cubic feet per minute per square foot (cfm/sf) outside air or as determined by
ASHRAE 62.1-2007, whichever is greater, until a total of 14,000 cubic feet per square foot of
building has been delivered to the space.
Conduct baseline IAQ testing, after construction and before occupancy, in accordance with
"Environmental Protection Agency (EPA) Compendium of Methods for the Determination of Air
Pollutants in Indoor Air".
Other:
| Low-Emitting Materials - Adhesives and Sealants |  | Low Emitting Adhesives and Sealants
Use low-emitting (low or no volatile organic compound (VOC)) materials on at least 75% of interior
| 4.3 Low-Emitting Materials and Products | products by cost or surface area.
| (Guiding Principles for Sustainable Federal Buildings 2020) |  | Low VOC carpet adhesive
Low VOC carpet pad adhesive
Low VOC wood flooring adhesive
Low VOC rubber floor adhesive
Low VOC subfloor adhesive
Low VOC ceramic tile adhesive
Low VOC vinyl composition tile (VCT) and asphalt adhesive
Low VOC drywall and panel adhesive
Low VOC cove base adhesive
Low VOC multipurpose construction adhesive
Low VOC structural glazing adhesive
Low VOC polyvinyl chloride (PVC) glue
Low VOC chlorinated polyvinyl chloride (CPVC) glue
Low VOC acrylonitrile butadiene styrene (ABS) glue
Low VOC plastic welding
Low VOC plastic primer
Low VOC contact adhesive
Low VOC structural wood member adhesive
Low VOC sheet applied rubber lining
Low VOC top and trim adhesive
Low VOC architectural sealant
Low VOC nonmembrane roof sealant
Low VOC roadway sealant
Low VOC single ply roof membrane sealant
Low VOC sealant primer, architectural nonporous
Low VOC sealant primer, architectural porous
Low VOC metal to metal adhesive
Low VOC plastic foam adhesive
Low VOC porous material (except wood) adhesive
Low VOC wood adhesive
Low VOC fiberglass adhesive
Other:
| Low-Emitting Materials - Paints and Coatings |  | Low Emitting Paints & Coatings
Use low-emitting (low or no volatile organic compound (VOC)) materials on at least 75% of interior
| 4.3 Low-Emitting Materials and Products | products by cost or surface area.
| (Guiding Principles for Sustainable Federal Buildings 2020) |  | Low VOC bond breakers
Low VOC varnish
Low VOC lacquer
Low VOC concrete curing compounds
Low VOC dry-fog coatings
Low VOC fire-retardant coatings
Low VOC flat paints
Low VOC floor coatings
Low VOC nonflat high gloss coatings
Low VOC nonflat non-high gloss coatings
Low VOC quick dry enamels
Low VOC shellac
Low VOC stains
Paints are Green Seal (GS) Standard GS-11 compliant.
Clear wood finishes are South Coast Air Quality Management District (SCAQMD) Rule 113 compliant.
All anti-corrosive and anti-rust paints are GS Standard GC-03 compliant.
Other:
| Low-Emitting Materials - Flooring Materials |  | Low Emitting Flooring Systems
Carpet meets testing and product requirements of Carpet and Rug Institute Green Label Plus Program.
| 4. Enhance the Indoor Environment |  | All carpet cushion meet requirements of Carpet and Rug Institute Green Label Program.
| (Guiding Principles for Sustainable Federal Buildings 2020) |  | Hard surface flooring must be compliant with FloorScore.
Other:
| Moisture Control |  | Moisture Control
Building envelope assemblies conform to recommended practices on
| 4.5 Moisture and Mold Control |  | DSC Workflows Design Standards > Architectural Standards
| (Guiding Principles for Sustainable Federal Buildings 2020) |  | Building envelope assemblies conform to moisture control. (See ASHRAE Fundamentals 2021.)
Building envelope assemblies conform to Moisture Control Handbook (Lstiburek and Carmody 1991)
| EO 14057 Catalyzing Clean Energy Industries and Jobs Through Federal Sustainability |  | for recommended practices.
Other:
| Controllability of Systems - Lighting |  | Controllability of Lighting
Individual lighting control for building occupants.
| 4. Enhance the Indoor Environment |  | Separate lighting controls for shared multi-occupant spaces to meet group needs.
| (Guiding Principles for Sustainable Federal Buildings 2020) |  | Other:
| Thermal Comfort Design |  | Thermal Comfort Design
Building meets requirements of ASHRAE 55-2020.
| 4.1 Ventilation and Thermal Comfort |  | Other:
(Guiding Principles for Sustainable Federal Buildings 2020)
| Daylighting and Lighting Controls |  | Daylight
Provide daylight control for interior lighting.
| 4.2 Daylight and Lighting Controls |  | Install interior light shelf to project daylighting further into spaces.
| (Guiding Principles for Sustainable Federal Buildings 2020) |  | Install exterior light shelf for glare control.
Install fixed exterior shading devices for glare control.
Provide windows in occupied spaces for occupants to obtain daylight.
Provide skylights in occupied spaces for occupants to obtain daylight.
Task lighting
Other:
| Radon |  | Radon
New Construction - Incorporate radon resistant construction techniques.
| Radon-Resistant Construction Basics and Techniques |  | Install course gravel layer, perforated pipe, or collection mat below foundation.
Install heavy duty plastic sheeting or vapor retarder over gravel layer.
| 4.4 Radon Mitigation |  | Install vent pipe vertically from gravel to roof.
| (Guiding Principles for Sustainable Federal Buildings 2020) |  | Seal all openings and cracks in concrete foundations and walls with polyurethane caulk.
Install electrical J-Box (Junction-Box) for use with a vent fan.
Major Renovations
Test for radon prior to construction.
For levels greater than or equal to 4pCi/L (Picocurie per Liter), employ radon mitigation techniques.
| Integrated Pest Management |  | Integrated Pest Management
Potential pest species have been discussed with NPS and building design incorporates strategies
| NPS Integrated Pest Management Program |  | to manage identified pests.
Other:
4.8 Integrated Pest Management
(Guiding Principles for Sustainable Federal Buildings 2020)
| Occupant Health and Wellness |  | Occupant Health and Wellness
Building or site-wide health and fitness programs
| WBDG Promote Health and Well-Being |  | Fitness center
Convenient access to healthy dining options
| 4.9 Occupant Health and Wellness |  | Active/ergonomic work stations
| (Guiding Principles for Sustainable Federal Buildings 2020) |  | Bicycle commuter facilities
Water bottle filling stations
Access to daylight
Indoor plants
Exterior views
Other:
ADDITIONAL FEDERAL DESIGN IMPERATIVES
| Risk Assessment |  | Risk Assessment
This building does not include critical infrastructure.
| 6.1 Risk Assessment |  | This building does include critical infrastructure.
| (Guiding Principles for Sustainable Federal Buildings 2020) |  | Use sustainable landscape design principles.
| Flood Plain Considerations |  | Flood Plain
| For mission critical buildings, adjust base flood elevation by 3 feet. For non-mission | Provide explanations:
| critical buildings, adjust base flood elevation by 2 feet. | 1
2
| 6.2 Building Resilience and Adaptation | 3
| (Guiding Principles for Sustainable Federal Buildings 2020) | 4
5
| EO 13690 - Establishing a Federal Flood Risk Management Standard and a Process for | 6
| Further Soliciting and Considering Stakeholder Input | 7
| Facility Design / Natural Hazards |  | Facility Design / Natural Hazards
| Incorporate resilience measures to mitigate the impacts of climate change and | Perform hazard assessment. Hazards identified for this project:
| natural hazards as identified on the Natural Hazards Checklist. |  | Earthquake
Landslide/Avalanche
| Natural Hazard Checklist |  | Permafrost
| (Begins on page 6 of Addressing Climate Change and Natural Hazards Handbook) |  | Cave/Karst
Shrink/Swell Soils
| 6.2 Building Resilience and Adaptation |  | Coastal Storm Surge
| (Guiding Principles for Sustainable Federal Buildings 2020) |  | Tsunami
Riverine Flood
Flash Flood
Hurricane
Tornado
Wildfire
Volcanic Eruption
Hydro-Thermal Activity (e.g. geysers)
Pest Infestation
Hazards do not occur due to geological setting.
Other:
| Facility Adaptation |  | Facility Adaptation
| For existing buildings, undergo modernization and take action to mitigate identified | Provide explanations:
| physical risks. See Natural Hazards Checklist. | 1
2
| National Hazard Checklist | 3
| (Begins on page 6 of Addressing Climate Change and Natural Hazards Handbook) | 4
5
| 6.2 Building Resilience and Adaptation | 6
(Guiding Principles for Sustainable Federal Buildings 2020)
TOP 5 SUSTAINABILITY FEATURES
| Top 5 Sustainability Features |  | Project's Top 5 Sustainable Design Features
| List the project's top 5 sustainable design features. | 1
2
3
4
5
SUSTAINABILITY SCOPE
Notes: Enter any additional details regarding the project's sustainability scope.

## Lists (hidden)
X
None
Silver
Certified
Gold
Platinum
Formal
Informal
New Building
Building Renovation
No Building
Line Item
Planning, Design, & Construction
2009 Recovery
Other