## Intro & Definitions
CC-GRTE001-27 |  | Appendix F: Deferred Maintenance Work Order List
The Concessioner must cure, within the first two years of the Contract’s term, all deferred maintenance (DM) and legislatively mandated work (LM) for Concession Facilities, called collectively simply deferred maintenance or DM. In the first year of the Draft Contract, the Service will work with the Concessioner to develop a prioritized and comprehensive list of task orders, developed from the list provided here. Below is a point-in-time list of work orders which the Service believes properly represents the DM and LM that will need to be cured at the start of the Contract. Conditions and quantities may vary from the descriptions and quantities provided herein.
Definitions of Work Subtypes Acronyms
Acronym | Asset Management Term | NPS Definition
CR | Component Renewal | The planned Replacement of a Component at the end of its Useful Life. Component Renewal examples include the replacement of foundations, building frames, window frames, windows, doors, sheathing, subfloors, drainage and roofs; the replacement of building systems such as electrical distribution systems, built-in heating and cooling systems, and plumbing systems; and the rehabilitation of Components of historic Concession Facilities. Component Renewal includes the deconstruction of the existing Component and the Replacement of that Component with a new Component of equal or superior capability and performance. These actions recur on a periodic cycle of greater than seven (7) years.
DM | Deferred Maintenance | Maintenance that was not timely or properly conducted. Continued Deferred Maintenance will result in Deficiencies.
CRDM | Component Renewal Deferred Maintenance | Component Renewal work that was not performed when it was scheduled or should have been performed based on wear. The maintenance is, therefore, past due and delayed. Continued deferment of maintenance will result in Deficiencies
LMAC | Legislatively Mandated Accessibility | Faults or defects in an existing system/asset/equipment that must be corrected in response to accessibility legislation.
LMFS | Legislatively Mandated Fire Structure | Faults or defects in an existing system/asset/equipment that must be corrected in response to structural fire regulatory or code requirements.
LMLS | Legislatively Mandated Life Safety | Faults or defects in an existing system/Component/equipment that must be corrected in response to life and safety regulatory or code requirements
RMDM | Recurring Maintenance Deferred Maintenance | Recurring Maintenance that was not performed when it was scheduled or should have been performed based on wear. The maintenance is, therefore, past due and delayed. Continued deferment of maintenance will result in Deficiencies.

## GRTE001
Asset | Work Order | Asset Description | Work Subtype | Work Order Description | Priority Year
4243 |  | (CN) R - CBCG RT-215ZZ | CRDM | Replace Sign, replace rotted and damage + has passed its useful life. | 2027
4243 |  | (CN) R - CBCG RT-215ZZ | CRDM | Replace as it is past its useful life;36" x 16" Wood, Painted, Warning Sign, Routed. With 8" wood post, 6 LF. Located on entrance road leading to loops A through G. | 2027
4243 |  | (CN) R - CBCG RT-215ZZ | CRDM | Replace Sign Pole, past its useful life not anchored in ground. Located at RV dump station | 2027
4243 |  | (CN) R - CBCG RT-215ZZ | CRDM | Replace as it is past its useful life;36" x 6" Wood, Painted, Warning Sign, Routed. With (2) 6"x16" additional signs and a single 4" wood post, 8 LF. Located on entrance road near campground dump station. | 2027
4243 |  | (CN) R - CBCG RT-215ZZ | CRDM | Replace Sign, Rotted, Past useful life located at exit to RV campground. | 2027
4243 |  | (CN) R - CBCG RT-215ZZ | DM | Adjust drain culvert, poor drainage on to tent site located at N #295. 12" diameter corrugated steel, drain culvert, with 42"x26" cast iron grate with 16" deep concrete vault. 16 LF. | 2027
4243 |  | (CN) R - CBCG RT-215ZZ | DM | Repair and clean blocked culvert, near site N #292 #311 - catch basin at site number 311 does not have a termination area locate and needs repair. as does loop O at site 326. | 2027
4298 |  | (CN) R - GVCG - Roads RT-0202ZZ | CRDM | Replace sign, past useful life | 2027
4298 |  | (CN) R - GVCG - Roads RT-0202ZZ | CRDM | Replace as it is past its useful life;42" x 16" wood, painted, warning sign, with 2 x 4 post and in 8 sq. ft. of concrete. | 2027
4298 |  | (CN) R - GVCG - Roads RT-0202ZZ | DM | Replace Damage Sign, Located at the split of lube F your site to 92 | 2027
4298 |  | (CN) R - GVCG - Roads RT-0202ZZ | DM | Clean Blocked Culvert, Located under road near office at entrance to campground, near site 38, near site 67, site 72. Under road to W. Corridor Near Loop E, at entrance to loop A, on W. Corridor Rd. near site 222, | 2027
4298 |  | (CN) R - GVCG - Roads RT-0202ZZ | DM | Clean Blocked Culvert, At site 121 of loop B, entrance to Loop C, near site 124 of Loop C | 2027
4298 |  | (CN) R - GVCG - Roads RT-0202ZZ | DM | Clean Blocked Culvert, Located in Group loop north of comfort station and group site E | 2027
4298 |  | (CN) R - GVCG - Roads RT-0202ZZ | RMDM | Repaint Bollards are past their useful paint lifecycle, located near campsite 326 of Loop F, 332, for near the culvert in Loop F and site 352 | 2027
4298 |  | (CN) R - GVCG - Roads RT-0202ZZ | RMDM | Repaint Sign, past it’s repaint cycle, located north of the office prior to parking area on west side of road | 2027
4298 |  | (CN) R - GVCG - Roads RT-0202ZZ | RMDM | Repaint sign past useful paint lifecycle at Loop G split | 2027
4327 |  | (CN) R - DEADMANS Bar Float Spur, Unpaved, RT-222 | RMDM | Replace as it is past its useful life; Gravel, 3" Deep, Roadway/Street Surface, Located at Deadman's Bar | 2027
4343 |  | (CN) R - Jenny Lake Campground Roads RT-205 | DM | Remove Excessive Foliage, Asphalt, 3" Deep, Roadway/Street Surface, Located throughout campground | 2027
4343 |  | (CN) R - Jenny Lake Campground Roads RT-205 | RMDM | Repaint Gate, Past painting lifecycle, Swinging Gate, 30 LF of 2"x4" Galvanized steel piping, hinged to (2) 6" diameter, steel galvanized posts 12 LF, filled with concrete with cross braced steel piping. Painted. Located at entrance to campground. (1 ea.) | 2027
4433 |  | (CN) ML - Jenny Lake Campground Maintained Landscape | CRDM | Replace missing or dilapidated parking stop. 12" Wood Timber, Parking Stop, 10' long each, anchored to a pyramid shaped concrete block that is 8"x8" inch top and 8"x15" at the bottom and 12 inches deep at each end of the log. with 12" long bolts connecting the log to the concrete bases, located beside registration booth. | 2027
4433 |  | (CN) ML - Jenny Lake Campground Maintained Landscape | DM | Replace Dilapidated bollard at site 47 and site 37. 8" Wood, Painted, Bollards, log, and 42" tall, | 2027
4433 |  | (CN) ML - Jenny Lake Campground Maintained Landscape | DM | Repair campsite Marker that are leaning at sites: 3, 8, 11, 14, 15, 16, 21, 24, 27, 28, 30, 31, 32, 48, 49; 10" Wood Timber, Painted, Sign Pole, log, total length 6-foot ea. With Routed number at top. | 2027
4433 |  | (CN) ML - Jenny Lake Campground Maintained Landscape | DM | Replace dilapidated parking stops at the following campsites: two at site 1, 37, 47, 50, Replace one at 4, 8, 10, 16, 25, 35, 36 38, 42, 45, 48; 8" Wood Timber, Parking Stop, log 10' long with two 12 x 12 x 24 concrete anchors at each end. | 2027
4433 |  | (CN) ML - Jenny Lake Campground Maintained Landscape | DM | Replace damaged campsite marker at sites 4 (ants), 5, 9, 10, 17, 20, 22, 23, 33, 34, 35, 37, 47. 10" Wood Timber, Painted, Sign Pole, log, total length 6-foot ea. With Routed number at top. | 2027
4433 |  | (CN) ML - Jenny Lake Campground Maintained Landscape | DM | Replace missing parking stops at campsites 4, 21, 34, and 39. 8" Wood Timber, Parking Stop, log 10' long with two 12 x 12 x 24 concrete anchors at each end. | 2027
4433 |  | (CN) ML - Jenny Lake Campground Maintained Landscape | RMDM | Replenish depleted and missing gravel at all sites except accessible sites. 12' x 20' Gravel, 2" Deep, Parking Area, located every campsite which is not accessible. All sites but: 3, 5, 6. | 2027
9697 |  | (CN) B - GVCG - Office B0715 | CRDM | Replace as it is past its useful life; 16" x 23" Electric Wall Heater, Located on the south wall in the back office | 2027
9697 |  | (CN) B - GVCG - Office B0715 | CRDM | Replace as it is past its useful life; Toggle, Single Pole Switch, Located in the bathroom next to the door. | 2027
9697 |  | (CN) B - GVCG - Office B0715 | CRDM | Replace as it is beyond its useful life; 72" x 194" x 24" Concrete, Auxiliary Pad - Slab on Grade, 6-foot wide, same width as structure at 16’ 2". Located at south end of structure. 97 SF. | 2027
9697 |  | (CN) B - GVCG - Office B0715 | DM | Add screen to prevent pest intrusion. 16" X 8", Crawlspace Vent, Concrete block turned on side, 4 total, Located on east and west walls | 2027
9697 |  | (CN) B - GVCG - Office B0715 | DM | Replace missing door at hallway. 30" x 80" Hollow Core - Wood, Flat Slab, Standard Door Handle, Factory Finish, Standard Interior Door Located in the Hall that connects the front office from rear storage. | 2027
9697 |  | (CN) B - GVCG - Office B0715 | LMAC | Replace door lockset with on that does not require tight grasping, tight pinching or twisting of the wrist to operate as per ADAABAG Section 309.4; 30" x 77" Screen Door, Located on the South facade of the structure. | 2027
9697 |  | (CN) B - GVCG - Office B0715 | LMAC | Replace door lockset with on that does not require tight grasping, tight pinching or twisting of the wrist to operate as per ADAABAG Section 309.4; 30" x 77" Exterior Entrance Door, original skeleton key lock set and modern deadbolt, 5 panel built up. Located on the South facade of the structure. | 2027
9697 |  | (CN) B - GVCG - Office B0715 | LMAC | Replace door lockset with on that does not require tight grasping, tight pinching or twisting of the wrist to operate as per ADAABAG Section 309.4; 30" x 80" Exterior Entrance Door, Top half glass, lower half 3 panels wood. Located at front entry on the North facade of the structure. | 2027
9697 |  | (CN) B - GVCG - Office B0715 | LMAC | Replace lockset with one that does not require tight grasping, tight pinching or twisting of the wrist to operate as per ADAABAG Section 309.4; 24" x 80" Hollow Core - Wood, Flat Slab, Standard Door Handle, Factory Finish, Standard Interior Door, Located on the north wall of the dry storage area to the northeast closet | 2027
9697 |  | (CN) B - GVCG - Office B0715 | LMAC | Replace lockset with one that does not require tight grasping, tight pinching or twisting of the wrist to operate as per ADAABAG Section 309.4; 30" x 80" Solid Core - Wood, Flat Slab, Standard Door Handle, Factory Finish, Standard Interior Door, Located door to restroom. | 2027
9697 |  | (CN) B - GVCG - Office B0715 | LMAC | Replace lockset with one that does not require tight grasping, tight pinching or twisting of the wrist to operate as per ADAABAG Section 309.4; 30" x 80" Hollow Core - Wood, Flat Slab, Standard Door Handle, Factory Finish, Standard Interior Door, located in the Hall that connects the front office from rear storage. | 2027
9697 |  | (CN) B - GVCG - Office B0715 | LMAC | Replace lockset with one that does not require tight grasping, tight pinching or twisting of the wrist to operate as per ADAABAG Section 309.4; 32" x 80" Hollow Core - Wood, Divided Light, Lockset Hardware, Factory Finish, Specialty Door, Located in the northeast corner of the front office. Door is a divided light with the upper half is a 2 x 2 window glass single pane. Lock looks to be original. | 2027
9697 |  | (CN) B - GVCG - Office B0715 | LMAC | Relocate flush hand control to be on the open side of the water closet as per ADAABAG Section 604.6; Porcelain, with Tank, Floor Mounted, with Manual Handle Flush Valve, Water Closet, Located in the bathroom. | 2027
9697 |  | (CN) B - GVCG - Office B0715 | LMAC | Add protecting covering for the hot water and drainpipes under the accessible lavatory/sink in the rest room as per ADAABAG Section 606.5; 20" x 20" Porcelain, Wall Hung, Wall Mounted, Lavatory, Located in the bathroom | 2027
9697 |  | (CN) B - GVCG - Office B0715 | LMAC | Replace faucet with one that is easy to operate with one hand and not require tight grasping, pinching, or twisting of the wrist as per ADAABAG Section 606.4, 308; Chrome Finish, Faucet - Single Valve, Located at the lavatory in the bathroom. | 2027
9697 |  | (CN) B - GVCG - Office B0715 | LMCO | Replace original outlet in front of the water closet with a GFCI outlet or change the breaker to be GFCI protected. Grounded, 3-Wire Receptacle Located throughout the building. Per NEC Reference Code Section 210.8 (B), (C) | 2027
9697 |  | (CN) B - GVCG - Office B0715 | LMLS | Replace missing switch plate cover. Rocker Switch, 3-Way Switch Located in the bathroom next to the door. | 2027
9720 |  | (CN) CBV-502 Comfort Stations Loop A (B-B0225) | DM | Repair leaking faucet. 12" x 16" Chrome Finish, Faucet - Dual Handle Located on service sink in the service sink room. | 2027
9728 |  | (CN) B - GVCG - B0718 Campground Comfort Station A Loop | DM | Repair leaking pipe located in the back of the utility chase. 1-1/2" Copper, Hot & Cold Water, Supply Piping. | 2027
9732 |  | (CN) B - Jenny Lake Campground Comfort Station (HS-0039) | CRDM | Replace as it is past its useful life; Chrome Finish, Faucet - Single Valve, the valve is a twist valve. Located along the east wall of the men’s room in the southeast corner of the bathroom. One located in the women’s restroom in the northeast corner | 2027
9732 |  | (CN) B - Jenny Lake Campground Comfort Station (HS-0039) | CRDM | Restore Wood, Glazed Window by removing old finish then putty and repair minor damages and replace warped or damaged pieces with like cut and species with matching color. In accordance with historic preservation standards, 30" X 60", Wood, Glazed Window, Fixed, Single Pane, Painted, with 12 lites, (This component is part of the historic fabric of the building), Located at east and west ends of structure over door at gable | 2027
9732 |  | (CN) B - Jenny Lake Campground Comfort Station (HS-0039) | DM | Repair rafters ends using replacement splices on south eaves. 6", Rafters - Wood, Pitched Roof Construction, with spaced slats decking, Space 32 inches on center with 1x10 and 1x8 slats, 10 feet long each, and painted where on the exterior and within bathrooms., (This component is part of the historic fabric of the building), Located at entire roof of comfort station | 2027
9732 |  | (CN) B - Jenny Lake Campground Comfort Station (HS-0039) | LMAC | Adjust self-closing device so that from an open position of 90 degrees, the door will take at least 5 seconds to move to a point 12degress from the latch, measured to the leading edge of the door, as per ADAABAG Section 404.2.8.1; 3" x 89" Wood, with Self-Closing Device, Painted, Exterior Entrance Door Built up door with 1x4 tongue and groove on inside, 1x8 planks exterior facing, and 1x4 vertical battens and diagonal at front. Three barn door hinges, 2 pull handles, and lock hasp. Located at east and west entries. | 2027
9732 |  | (CN) B - Jenny Lake Campground Comfort Station (HS-0039) | LMAC | Adjust stall door in the women's side in the Accessible stall so that it is self-closing, as per ADAABAG Section 604.8.1.2; 52" x 82" x 58" Metal, Fabricated Toilet Partition, with (1) 36"x58" door | 2027
9732 |  | (CN) B - Jenny Lake Campground Comfort Station (HS-0039) | LMAC | Relocate flush control valve so that it is located on the open side of the water closet as per ADAABAG Section 604.6. Replace at end of useful life: Porcelain, Tankless, Floor Mounted, with Manual Handle Flush Valve, Water Closet, Located in the women’s restroom. | 2027
9732 |  | (CN) B - Jenny Lake Campground Comfort Station (HS-0039) | LMAC | Adjust self-closing faucet so that is does remain open for at least 10 seconds as per ADAABAG Section 606.4; Chrome Finish, Faucet - Single Valve, Push Moen faucet. Located in the men’s restroom along the south wall in front of the accessible stall. | 2027
9732 |  | (CN) B - Jenny Lake Campground Comfort Station (HS-0039) | RMDM | Repaint exterior door as finishes have deteriorated. 33" x 89" Wood, with Self-Closing Device, Painted, Exterior Entrance Door Built up door with 1x4 tongue and groove on inside, 1x8 planks exterior facing, and 1x4 vertical battens and diagonal at front. Three barn door hinges, 2 pull handles, and lock hasp. Located at east and west entries. (This component is part of the historic fabric of the building). | 2027
9791 |  | (CN) CBV-009 Marina Comfort Station (B250) | LMAC | Replace door hardware so it will not require tight grasping, tight pinching or twisting of the wrist to operate as per ADAABAG Section 309.4. 36" x 84" Metal, with Self-Closing Device, Lockset with Key, Painted, Exterior Entrance Door, Located to the men’s and women’s restroom. | 2027
9791 |  | (CN) CBV-009 Marina Comfort Station (B250) | LMAC | Adjust door closer so that the force to push or pull open the door is a maximum of 5 pounds; as per ADAABAG Section 404.2.9. 36" x 84" Metal, with Self-Closing Device, Lockset with Key, Painted, Exterior Entrance Door, Located to the men’s and women’s restroom. | 2027
9791 |  | (CN) CBV-009 Marina Comfort Station (B250) | LMAC | Replace door hardware with one that does not require tight grasping, pinching, or twisting of the wrist to operate as per ADAABAG Section 309.4. 36" x 84" Wood, with Self-Closing Device, Lockset with Key, Painted, Exterior Entrance Door, With a 20"x36" view window and a 16"x6" vent. Located to the utility room. (This component is part of the historic fabric of the building). | 2027
9791 |  | (CN) CBV-009 Marina Comfort Station (B250) | LMAC | Adjust door closer so that the force required to push or pull open the door is a maximum of 5 pounds; as per ADAABAG Section 404.2.9. 36" x 84" Wood, with Self-Closing Device, Lockset with Key, Painted, Exterior Entrance Door, With a 20"x36" view window and a 16"x6" vent. Located to the utility room. (This component is part of the historic fabric of the building). | 2027
9791 |  | (CN) CBV-009 Marina Comfort Station (B250) | LMAC | Add protecting covering for the hot water and drainpipes under the accessible lavatory/sink in the men's and women's rest rooms as per ADAABAG Section 606.5. 20" x 20" Porcelain, Wall Hung, Wall Mounted, Lavatory, Located (1) in the men’s and (1) in the women’s restroom. | 2027
9791 |  | (CN) CBV-009 Marina Comfort Station (B250) | LMAC | Adjust urinal so that the rim is a maximum of 17" above the floor; as per ADAABAG Section 605.2. and adjust flush control so it is mounted no higher than 44" above the floor; per ADAABAG Section 605.4; 18" x 24" Porcelain, Tankless, Wall Mounted, with Manual Handle Flush Valve, Urinal, Located in the men's restroom. | 2027
9791 |  | (CN) CBV-009 Marina Comfort Station (B250) | LMAC | Replace faucet with on that is accessible and can be operated with one hand and not require tight grasping, pinching, or twisting of the wrist and requires less than 5 pounds to operate, and that the valve remains open for at least 10 seconds as per ADAABAG Section F213.3.4 & Section 605.4, 309. and Section 606.44" Chrome Finish, Faucet - Single Valve, Located on sinks in the men’s restroom. | 2027
9791 |  | (CN) CBV-009 Marina Comfort Station (B250) | RMDM | Refinish floors in men’s and women’s restrooms as they are past the useful life. 6" Concrete, painted, Standard Slab on Grade Located in the men’s and women’s restroom and in the utility room. | 2027
31650 |  | (CN) R - Jenny Lake Campground Parking RT 986P | DM | Remount parking stops located in the parking area. 12" diameter Parking Stop, Located at the three parking stalls, with one behind the building: of the parking area. With 8“ x 24“ concrete anchors 20 inches deep. 8 total | 2027
31650 |  | (CN) R - Jenny Lake Campground Parking RT 986P | RMDM | Re-stripe three parking stalls and Accessible parking stall. | 2027
35802 |  | (CN) R - CBCG Parking RT-967ZZ | CRDM | Replace Curbing, past its useful life; 10" diameter Wood timber, curbing around RV dump and in parking lot adjacent to Loop A. 280 LF | 2027
35802 |  | (CN) R - CBCG Parking RT-967ZZ | CRDM | Replace Parking Barriers, Past useful life; 10" diameter Wood timber, curbing near RV dump adjacent to Loop I, (120) LF | 2027
35802 |  | (CN) R - CBCG Parking RT-967ZZ | RMDM | Re-stripe parking stalls and crosswalk. Located at parking lot adjacent to Lupe. | 2027
36117 |  | (CN) R - GVCG - Amphitheater Parking RT 985P | DM | Add Missing Bollards, located at east entrance to each side of the roadway and two additional at roadway as it opens into parking area at East End also. | 2027
36117 |  | (CN) R - GVCG - Amphitheater Parking RT 985P | DM | Re-Anchor Parking Stop, Located on the north side at the east end of the parking area | 2027
36117 |  | (CN) R - GVCG - Amphitheater Parking RT 985P | DM | Remove debris to allow parking stops to be visible along the entire south side of the parking area | 2027
36117 |  | (CN) R - GVCG - Amphitheater Parking RT 985P | RMDM | Repaint bollards as they are past useful painting lifecycle. 10" diameter Wood, Bollards, 24" above ground, 24" buried. 4 LF per post. 152 Total LF. Located on both sides of the roadways at both entrances to the parking area. Painted | 2027
36124 |  | (CN) R - GVCG - Dump station RT 984P | CRDM | Replace 8 foot long damage parking stop as it is past the end of its useful life located on the north end near the dump station. | 2027
36124 |  | (CN) R - GVCG - Dump station RT 984P | DM | Repair pothole located at the north end of the dump station route | 2027
36124 |  | (CN) R - GVCG - Dump station RT 984P | DM | Replace Missing and Damaged Bollards, three located on the south end and one located on the north end. | 2027
36146 |  | (CN) R - GVCG - Ranger Station Parking RT 983P | DM | Replace damaged Ballard, make vertical leaning Bollard. | 2027
51530 |  | (CN) B - GVCG - B0719 Campground Comfort Station B Loop East | DM | Repair multiple leaks at connections in the utility chase. 1-1/2" diameter Copper, Hot & Cold Water, Supply Piping, Located main supply into the building. | 2027
51530 |  | (CN) B - GVCG - B0719 Campground Comfort Station B Loop East | LMCO | Extend plumbing vent through the roof to be a minimum of 6" and a maximum height of 24" per UPC 906.1; 6" diameter Cast Iron, Waste & Vent Piping, located main waste line of the building. | 2027
51530 |  | (CN) B - GVCG - B0719 Campground Comfort Station B Loop East | RMDM | Repaint concrete slab as it is past due; Concrete, 6 Thick, painted, Standard Slab on Grade, Located floor for entire building except utility chase. | 2027
51531 |  | (CN) B - GVCG - B0720 Campground Comfort Station B Loop West | DM | Replace missing gravel on roof above women's restroom; Tar & Gravel, Roof Finish, With 2-inch drip edge around the perimeter of the roof. Located over to the entire roof. (This component is part of the original fabric of the building). | 2027
51531 |  | (CN) B - GVCG - B0720 Campground Comfort Station B Loop West | DM | Repair leaks in water line at connections in the utility chase; 1-1/2" diameter Copper, Hot & Cold Water, Supply Piping, Located main supply into the building. | 2027
51531 |  | (CN) B - GVCG - B0720 Campground Comfort Station B Loop West | LMCO | Extend plumbing vent through roof to be a minimum of 6" and a maximum of 24" above the roof as per the UPC 906.1; 6" diameter Cast Iron, Waste & Vent Piping, located main waste line of the building. | 2027
51531 |  | (CN) B - GVCG - B0720 Campground Comfort Station B Loop West | RMDM | Repaint concrete floors as they are past due; Concrete, 6 Thick, painted, Standard Slab on Grade, Located floor for entire building except utility chase. | 2027
51531 |  | (CN) B - GVCG - B0720 Campground Comfort Station B Loop West | RMDM | Repaint soffit board as it is beyond time; 2" x 4" Painted, Soffit Covering, laid horizontally Soffit trim at front and back of building 56 LF. (This component is part of the original fabric of the building). | 2027
51532 |  | (CN) B - GVCG - B0721 Campground Comfort Station C Loop | DM | Repair roof at ridge line where cracks are present and replace missing gravel on roof; Tar & Gravel, With 2-inch drip edge around the perimeter of the roof. Located over to the entire roof. (This component is part of the original fabric of the building). | 2027
51532 |  | (CN) B - GVCG - B0721 Campground Comfort Station C Loop | DM | Repair leaks in water line at connections located in the utility chase; 1-1/2" diameter Copper, Hot & Cold Water, Supply Piping, Located main supply into the building. | 2027
51532 |  | (CN) B - GVCG - B0721 Campground Comfort Station C Loop | RMDM | Repaint concrete floors as they are past due; Concrete, 6 Thick, painted, Standard Slab on Grade, Located floor for entire building except utility chase. | 2027
51533 |  | (CN) B - GVCG - B0722 Campground Comfort Station D Loop East | DM | Repair leaks in water line at connections in the utility chase; 1-1/2" diameter Copper, Hot & Cold Water, Supply Piping, Located main supply into the building. | 2027
51533 |  | (CN) B - GVCG - B0722 Campground Comfort Station D Loop East | LMCO | Extend plumbing vent so that it is a minimum of 6" and a maximum of 24" above the roof line, as per UPC 906.1; 6" diameter Cast Iron, Waste & Vent Piping, located main waste line of the building. | 2027
51533 |  | (CN) B - GVCG - B0722 Campground Comfort Station D Loop East | RMDM | Repaint concrete floors as they are past due; Concrete, 6 Thick, painted, Standard Slab on Grade, Located floor for entire building except utility chase. | 2027
51534 |  | (CN) B - GVCG - B0723 Campground Comfort Station D Loop West | DM | Repair non-working urinal. 24" Porcelain, Tankless, Wall Mounted, Urinal Located in the men’s restroom. | 2027
51534 |  | (CN) B - GVCG - B0723 Campground Comfort Station D Loop West | LMAC | Adjust door closer so that the door will take at least 5 seconds to move from a 90-degree position to a point 12 degrees from the latch, as per ADAABAG Section 404.2.8.1; 36" x 80" Metal, with Self-Closing Device, Deadbolt, Painted, Exterior Entrance Door, With pull handle and push plate. Located doors into the men’s and women’s restroom. | 2027
51534 |  | (CN) B - GVCG - B0723 Campground Comfort Station D Loop West | LMAC | Adjust Door closer so that the maximum force to pull or push open the door is a maximum of 5 pounds; as per ADAABAG Section 309.4.and 404.2.9; 36" x 80" Metal, with Self-Closing Device, Deadbolt, Painted, Exterior Entrance Door, With pull handle and push plate. Located doors into the men’s and women’s restroom. | 2027
51534 |  | (CN) B - GVCG - B0723 Campground Comfort Station D Loop West | LMAC | Adjust door closer so that the door will take at least 5 seconds to move from a 90-degree position to a point 12 degrees from the latch, as per ADAABAG Section 404.2.8; 36" x 80" Metal, with Self-Closing Device, Deadbolt, Painted, Exterior Entrance Door, with a 20"x 24" view window and pull handle and push plate. Located door to service sink room. | 2027
51534 |  | (CN) B - GVCG - B0723 Campground Comfort Station D Loop West | LMAC | Adjust Door closer so that the maximum force to pull or push open the door is a maximum of 5 pounds; as per ADAABAG Section 309.4.and 404.2.9; 36" x 80" Metal, with Self-Closing Device, Deadbolt, Painted, Exterior Entrance Door, with a 20"x 24" view window and pull handle and push plate. Located door to service sink room. | 2027
51534 |  | (CN) B - GVCG - B0723 Campground Comfort Station D Loop West | LMAC | Adjust grab bar in the men's restroom so that the center line of the grab bar is positioned a minimum of 12" to the center line of the toilet as per ADAABAG Section 604.5.2; 1 1/2" x 36" Stainless Steel, Grab Bar, Located (1) in the men’s accessible stall and (1) in the women’s accessible stall behind the water closet. | 2027
51534 |  | (CN) B - GVCG - B0723 Campground Comfort Station D Loop West | LMAC | Adjust stall door so that it will close completely as per ADAABAG Section 604.8.1.2; 104" x 58" x 60" Metal, Fabricated Toilet Partition, With a 36"x58" door. Located in the men’s restroom. | 2027
51534 |  | (CN) B - GVCG - B0723 Campground Comfort Station D Loop West | LMAC | Add pull handle on the exterior of the stall door as per ADAABAG Section 604.8.1.2 and 404.2.7. 104" x 58" x 60" Metal, Fabricated Toilet Partition, With a 36"x58" door. Located in the men’s restroom. | 2027
51534 |  | (CN) B - GVCG - B0723 Campground Comfort Station D Loop West | LMAC | Adjust coat hook to be a maximum height of 48" as per ADAABAG Section 308.3, 603.4; 104" x 58" x 60" Metal, Fabricated Toilet Partition, With a 36"x58" door. Located in the men’s restroom. | 2027
51534 |  | (CN) B - GVCG - B0723 Campground Comfort Station D Loop West | LMAC | Adjust stall door so that it will close completely as per ADAABAG Section 604.8.1.2; 104" x 84" x 60" Metal, Fabricated Toilet Partition, with a 36"x58" door, located in the women’s restroom. | 2027
51534 |  | (CN) B - GVCG - B0723 Campground Comfort Station D Loop West | LMAC | Add pull handle on both sides of the stall door as per ADAABAG Section 604.8.1.2 and 404.2.7. 104" x 84" x 60" Metal, Fabricated Toilet Partition, with a 36"x58" door, located in the women’s restroom. | 2027
51534 |  | (CN) B - GVCG - B0723 Campground Comfort Station D Loop West | LMAC | Adjust coat hook to be a maximum height of 48" as per ADAABAG Section 308.3, 603.4; 104" x 84" x 60" Metal, Fabricated Toilet Partition, with a 36"x58" door, located in the women’s restroom. | 2027
51534 |  | (CN) B - GVCG - B0723 Campground Comfort Station D Loop West | LMAC | Adjust flush control valve so that is mounted no higher than 44" above the ground as per ADAABAG Section 605.4; 24" Porcelain, Tankless, Wall Mounted, Urinal, Located in the men’s restroom. | 2027
51534 |  | (CN) B - GVCG - B0723 Campground Comfort Station D Loop West | LMAC | Move water closet so that the center of the water closet is between 16"-18" from the closest wall as per ADAABAG Section 604.2; Porcelain, with Tank, Wall Mounted, Water Closet, With auto sensor. Located in the men’s and women’s restrooms in the handicap stalls. | 2027
51537 |  | (CN) B - GVCG - B0726 Campground Comfort Station F Loop East | DM | Repair urinal in men's restroom that is not working; 18" x 24" Porcelain, Wall Mounted, with Manual Handle Flush Valve, Urinal, Located in the men's restroom. | 2027
51537 |  | (CN) B - GVCG - B0726 Campground Comfort Station F Loop East | LMCO | Extend plumbing stack so that it is between a minimum of 6" and a maximum of 24" as per the UPC 906.1; 4" diameter Cast Iron, Waste & Vent Piping, Includes plumbing vent through the roof. | 2027
51538 |  | (CN) B -GVCG- B0727 Campground Comfort Station F Loop West | DM | Repair urinal that is currently not working; 18" x 24" Porcelain, Wall Mounted, with Manual Handle Flush Valve, Located in the men's restroom. | 2027
51538 |  | (CN) B -GVCG- B0727 Campground Comfort Station F Loop West | DM | Replace damaged concrete cap on top of drinking fountain; 34" x 36" x 18" Drinking Fountain, built with 4"x16" CMU block cut faced with mortar and a 4" think concrete cap single 10" stainless steel bowl. Located in front of the comfort station. | 2027
51538 |  | (CN) B -GVCG- B0727 Campground Comfort Station F Loop West | LMCO | Extend plumbing vent stack so that it is between a minimum of 6" and a maximum of 24" above the roof line, as per the UPC 906.1; 4" diameter Cast Iron, Waste & Vent Piping, Includes plumbing vent through the roof. | 2027
51540 |  | (CN) B - GVCG - B0729 Campground Comfort Station G Loop West | DM | Repair leak in main water line at connections to water closets in the utility room; 1-1/2" diameter Galvanized, Hot & Cold Water, Supply Piping, located main water line into the building located in the utility chase. | 2027
51541 |  | (CN) B - GVCG - B0730 Campground Comfort Station Group East | DM | Repair leak in main water line where it is leaking at connections in the utility chase; 1-1/2" diameter Galvanized, Hot & Cold Water, Supply Piping, located main water line into the building located in the utility chase. | 2027
51541 |  | (CN) B - GVCG - B0730 Campground Comfort Station Group East | LMCO | Extend plumbing vent stack pipe so that it extends a minimum of 6" but not more than 24" above the roof line as per the UPC 906.1; 4" diameter Cast Iron, Waste & Vent Piping, Includes plumbing vent through the roof. | 2027
51542 |  | (CN) B - GVCG - B0731 Campground Comfort Station Group West | DM | Repair leak in main water line at connections in the utility chase; 1-1/2" diameter Galvanized, Hot & Cold Water, Supply Piping, located main water line into the building located in the utility chase. | 2027
51542 |  | (CN) B - GVCG - B0731 Campground Comfort Station Group West | LMCO | Extend plumbing vent stack so that it is a minimum of 6" and a maximum of 24" above the roof line, as per the UPC section 906.1; 4" diameter Cast Iron, Waste & Vent Piping, Includes plumbing vent through the roof. Main waste line throughout the building. | 2027
51542 |  | (CN) B - GVCG - B0731 Campground Comfort Station Group West | LMLS | Fill in rodent holes located on the men's side of the building. CMU - Concrete Masonry Unit, Foundation Wall, 8"x16" CMU Block. 36" tall. Located around the perimeter of the building and under interior walls on top of the continuous footing. (119 LF). | 2027
52707 |  | (CN) CBV-503 Comfort Stations Loop B (B-B0224) | DM | Repair non-working water closet located in the women's restroom; Porcelain, Tankless, Wall Mounted, with Manual Handle Flush Valve, Water Closet, Located (2) in the men’s and (3) in the women’s restrooms. | 2027
52707 |  | (CN) CBV-503 Comfort Stations Loop B (B-B0224) | DM | Repair leaks in main water line at connections located in the utility chase; Copper, 1 1/2 Diameter, Hot & Cold Water, Supply Piping, Main line to building. | 2027
52707 |  | (CN) CBV-503 Comfort Stations Loop B (B-B0224) | LMCO | Repair door of electrical panel that does not latch as per NEC Code reference 406.5 (F); Metal Panel Box, Square D brand, with, 12 Breakers, 100 Amp/3 Wire System, Main Electrical Service Panel, Located in the utility chase. | 2027
52710 |  | (CN) CBV-505 Comfort Stations Loop D-1(B-B0221) | DM | Repair leaking faucet in service sink room; 12" x 16" Chrome Finish, Faucet - Dual Handle, Located on service sink in the service sink room. | 2027
52710 |  | (CN) CBV-505 Comfort Stations Loop D-1(B-B0221) | DM | Repair leaks in main water line at connections, located in the utility chase; Copper, 1 1/2 Diameter, Hot & Cold Water, Supply Piping, Main line to building. | 2027
52711 |  | (CN) CBV-506 Comfort Stations Loop D-2 (B-B0222) | DM | Repair hole in siding where rodents can enter the building located above women's entrance; 1" x 12" Wood Lap Siding, Lap, Painted, Exterior Siding Material, | 2027
52711 |  | (CN) CBV-506 Comfort Stations Loop D-2 (B-B0222) | DM | Repair broken window on men's restroom side; 40" x 32" Steel, Fixed, Single Pane, Glazed Window, With obscured glass. One on the men’s side. | 2027
52711 |  | (CN) CBV-506 Comfort Stations Loop D-2 (B-B0222) | DM | Repair broken view window in door to women's restroom, 36" x 84" Wood, with Self-Closing Device, Lockset with Key, Painted, Exterior Entrance Door, Built-up door. | 2027
52711 |  | (CN) CBV-506 Comfort Stations Loop D-2 (B-B0222) | DM | Repair leaks in main water line at connections, located in utility chase; Copper, 1 1/2 Diameter, Hot & Cold Water, Supply Piping, Main line to building. | 2027
52717 |  | (CN) CBV-508 Comfort Stations Loop F (B-B0234) | DM | Repair leaking main water pipe at connections located in the utility chase; Copper, 1 1/2 Diameter, Hot & Cold Water, Supply Piping, Main line to building. | 2027
52719 |  | (CN) CBV-509 Comfort Stations Loop G (B-B0231) | DM | Repair hole in soffit where rodents can enter the building at women's restroom; Plywood Sheeting, Painted, Soffit Covering, 1/2" thick. Located under an overhang around the perimeter of the roof. | 2027
52719 |  | (CN) CBV-509 Comfort Stations Loop G (B-B0231) | DM | Repair leaking main water line at connections, located in the utility chase; Copper, 1 1/2 Diameter, Hot & Cold Water, Supply Piping, Main line to building. | 2027
52720 |  | (CN) CBV-510 Comfort Stations Loop H (B-B0236) | DM | Repair leaking faucets in women’s restroom. Chrome Finish, Faucet - Single Valve Located on top of sinks in the women’s restroom. | 2027
52728 |  | (CN) CBV-511 Comfort Stations Loop I (B-B0237) | DM | Change swing of door so that it will not be blocked by the water pipes inside the utility chase; 30" x 84" Metal, Lockset with Key, Painted, Exterior Entrance Door, With 2 - 19"x12" vents at top and bottom of door. Door to utility chase. | 2027
52728 |  | (CN) CBV-511 Comfort Stations Loop I (B-B0237) | DM | Repair leaking water pipe at connections in the utility chase; Galvanized, 1 1/2 Diameter, Hot & Cold Water, Supply Piping. | 2027
52729 |  | (CN) CBV-512 Comfort Stations Loop J-1 (B-B0240) | DM | Repair hole in the siding over the men's entry where rodents can enter the building; T-111, Painted, Exterior Siding Material. | 2027
52729 |  | (CN) CBV-512 Comfort Stations Loop J-1 (B-B0240) | DM | Repair water leak in main water supply pipe at connections in the utility chase; Galvanized, 1 1/2 Diameter, Hot & Cold Water, Supply Piping, Main water supply into the building. | 2027
52730 |  | (CN) CBV-513 Comfort Stations Loop J-2 (B-B0238) | CRDM | Replace at end of useful life: Porcelain, Tankless, Floor Mounted, with Manual Handle Flush Valve, Water Closet, Located (2) in the men’s and (3) in the women’s restroom. | 2027
52730 |  | (CN) CBV-513 Comfort Stations Loop J-2 (B-B0238) | DM | Replace plywood on the back wall of the service sink room. Plywood, Painted. | 2027
52730 |  | (CN) CBV-513 Comfort Stations Loop J-2 (B-B0238) | DM | Repair leak at water shut off valve in the utility chase; Galvanized, 1 1/2 Diameter, Hot & Cold Water, Supply Piping. | 2027
52731 |  | (CN) CBV-514 Comfort Stations Loop K (B-B0239) | DM | Repair leak in main water line at the connections in the utility chase; Galvanized, 1 1/2 Diameter, Hot & Cold Water, Supply Piping, Main water supply into the building. | 2027
52731 |  | (CN) CBV-514 Comfort Stations Loop K (B-B0239) | RMDM | Refinish door as it is beyond time; 30" x 84" Metal, with Self-Closing Device, Deadbolt, Painted, Exterior Entrance Door, with push plate and pull handle; 8"x28" kick plate, and a 20"x24" view window with wire, and a 19"x12" vent. Located door to service sink room. | 2027
52732 |  | (CN) CBV-515 Comfort Stations Loop L (B-B0242) | DM | Repair non-working water closet in the men's restroom (last stall). Porcelain, Tankless, Floor Mounted, with Manual Handle Flush Valve, Water Closet. | 2027
52732 |  | (CN) CBV-515 Comfort Stations Loop L (B-B0242) | DM | Repair leaks in main water line at connections in the utility chase; Galvanized, 1 1/2 Diameter, Hot & Cold Water, Supply Piping, Main water supply into the building. | 2027
52733 |  | (CN) CBV-516 Comfort Stations Loop M-1 (B-B0255) | DM | Repair leaks in main water line at connections in the utility chase. Galvanized, 1 1/2 Diameter, Hot & Cold Water, Supply Piping. | 2027
52733 |  | (CN) CBV-516 Comfort Stations Loop M-1 (B-B0255) | RMDM | Refinish exterior doors as it is past due; 30" x 84" Metal, with Kick Plate, Deadbolt, Painted, Exterior Entrance Door, and push plate and pull handle, and self-closer. Located doors to the men’s and women’s restrooms. | 2027
52733 |  | (CN) CBV-516 Comfort Stations Loop M-1 (B-B0255) | RMDM | Refinish exterior door as it is past due; 30" x 84" Metal, with Self-Closing Device, Deadbolt, Painted, Exterior Entrance Door, with push plate and pull handle; 8"x28" kick plate, and a 20"x24" view window with wire, and a 19"x12" vent. Located door to service sink room. | 2027
52734 |  | (CN) CBV-517 Comfort Stations Loop M-2 (B-B0254) | DM | Repair broken window on men's restroom side; 42" x 18" Steel, Fixed, Single Pane, Painted, with aluminum screen, Glazed Window. | 2027
52734 |  | (CN) CBV-517 Comfort Stations Loop M-2 (B-B0254) | DM | Repair non-working urinal in the men's restroom. 18" x 38" Porcelain, Tankless, Cut in Floor, with Manual Handle Flush Valve, Urinal, Located in the men’s restroom. | 2027
52734 |  | (CN) CBV-517 Comfort Stations Loop M-2 (B-B0254) | DM | Repair leaks in main water line at connections in the utility chase; Galvanized, 1 1/2 Diameter, Hot & Cold Water, Supply Piping, Main water supply into the building. | 2027
52734 |  | (CN) CBV-517 Comfort Stations Loop M-2 (B-B0254) | LMCO | Extend roof plumbing vent to be a minimum of 6" and a maximum of 24" above roof. 4" diameter Cast Iron, Waste & Vent Piping.as per the UPC reference 906.1. | 2027
52735 |  | (CN) CBV-518 Comfort Stations Loop N (B-B0257) | DM | Repair broken window on men's restroom side; 42" x 18" Steel, Fixed, Single Pane, Painted, with aluminum screen, Glazed Window. | 2027
52735 |  | (CN) CBV-518 Comfort Stations Loop N (B-B0257) | DM | Repair leaks in main water line at connections in the utility chase; Galvanized, 1 1/2 Diameter, Hot & Cold Water, Supply Piping. | 2027
52735 |  | (CN) CBV-518 Comfort Stations Loop N (B-B0257) | LMCO | Extend Plumbing stack to be a minimum of 6" and a maximum of 24" above the roof as per the UPC reference 906.1. 4" diameter Cast Iron, Waste & Vent Piping. | 2027
52736 |  | (CN) CBV-519 Comfort Stations Loop O-1 (B-B0258) | DM | Repair leaks in main water line at connections in the utility chase; Galvanized, 1 1/2 Diameter, Hot & Cold Water, Supply Piping. | 2027
52736 |  | (CN) CBV-519 Comfort Stations Loop O-1 (B-B0258) | LMCO | Extend plumbing vent stack to be a minimum of 6" and a maximum of 24" above the roof; as per the UPC reference 906.1. 4" diameter Cast Iron, Waste & Vent Piping. | 2027
52736 |  | (CN) CBV-519 Comfort Stations Loop O-1 (B-B0258) | LMCO | Repair electrical panel door that does not latch as per the NEC reference 408.38; 14" x 15" Metal Panel Box, Square D brand, with, 12 Breakers, 100 Amp/3 Wire System, Main Electrical Service Panel, Located in the utility chase. | 2027
52737 |  | (CN) CBV-520 Comfort Stations Loop O-2 (B-B0259) | DM | Repair non-working water closet in first stall of women's restroom. Porcelain, Tankless, Floor Mounted, with Manual Handle Flush Valve, Water Closet. | 2027
52737 |  | (CN) CBV-520 Comfort Stations Loop O-2 (B-B0259) | DM | Repair leaks in main water line at connections in the utility chase; Galvanized, 1 1/2 Diameter, Hot & Cold Water, Supply Piping, Main water supply into the building. | 2027
52738 |  | (CN) CBV-521 Comfort Stations Loop P-1 (B-B0232) | DM | Repair leaking faucet in men's restroom, as it continually runs; Chrome Finish, Faucet - Single Valve, Located on top of sink in the men’s restroom. | 2027
52738 |  | (CN) CBV-521 Comfort Stations Loop P-1 (B-B0232) | DM | Replace entrance stoop in front of the women's restroom as it is beyond its useful life; 48" x 40" x 4" Concrete, Entrance Stoop. | 2027
52739 |  | (CN) CBV-522 Comfort Stations Loop P(Group) (B-B0261) | DM | Repair leak in main water line at connections in the utility chase; Galvanized, 1 1/2 Diameter, Hot & Cold Water, Supply Piping. | 2027
71115 |  | (CN) CBV-501 Fee Collection Kiosk (B-B1058) | CRDM | Replace gutter as it is past end of useful life. 4", Aluminum, Gutter & Downspout, 20 when your feet, painted, Located at edges of roof | 2027
71115 |  | (CN) CBV-501 Fee Collection Kiosk (B-B1058) | CRDM | Replace as it is past its useful life; 4" Aluminum, Gutter & Downspout, 20 Linear feet, painted. Located at edges of roof | 2027
71119 |  | (CN) CBV-523 Comfort Stations Loop P(Group) (B-B0260) | DM | Repair damaged ridge cap on the north side of the building; Aluminum Panel, Factory Finish, with 2" metal drip edge, Roof Finish, With metal roof cap. | 2027
71119 |  | (CN) CBV-523 Comfort Stations Loop P(Group) (B-B0260) | DM | Repair leaks on main water line at connections in the utility chase; Galvanized, 1 1/2 Diameter, Hot & Cold Water, Supply Piping. | 2027
71119 |  | (CN) CBV-523 Comfort Stations Loop P(Group) (B-B0260) | LMCO | Extend plumbing vent stack to be a minimum of 6" and a maximum of 24" above the roof as per the UPC reference 906.1; 4" diameter Cast Iron, Waste & Vent Piping, Includes vent stack. | 2027
82668 |  | (CN) CBV-001 Grocery Store/Gift Shop/Activities (CB-1) | CRDM | Replace Faucet as it is beyond its useful life; 6" x 6" Chrome Finish, Faucet - Lever Style, Located at coffee bar | 2027
82668 |  | (CN) CBV-001 Grocery Store/Gift Shop/Activities (CB-1) | CRDM | Replace Wood, fencing as it is beyond its useful life, with 3" logs that are 11’ tall located around NE section of the loading dock with steel posts at sides of gate and at corners gate is 8’ wide and 7’ tall (double gate) | 2027
82668 |  | (CN) CBV-001 Grocery Store/Gift Shop/Activities (CB-1) | CRDM | Replace as it is beyond its useful life; 8" diameter Valves & Gauges for, Main Fire Riser, Located in fire riser room | 2027
82668 |  | (CN) CBV-001 Grocery Store/Gift Shop/Activities (CB-1) | CRDM | Replace as it is beyond its useful life, Fire Alarm, With light. Located on the north end of the building just outside the fire riser room in between the men’s and women’s restroom | 2027
82668 |  | (CN) CBV-001 Grocery Store/Gift Shop/Activities (CB-1) | DM | Replace missing exterior door handle and lock. 48" x 80" Metal, Lockset with Key, Factory Finish, With 24" x 60" Louvered ventilation panel and lever style hardware. At upper mechanical room above the loading dock on the East side of building. | 2027
82668 |  | (CN) CBV-001 Grocery Store/Gift Shop/Activities (CB-1) | DM | Replace missing and damaged drywall located in generator room. Drywall, Unfinished, Interior Wall Covering Material, Located in the generator room. | 2027
82668 |  | (CN) CBV-001 Grocery Store/Gift Shop/Activities (CB-1) | LMAC | Adjust door closer so that the force required to push or pull open the door is a maximum of 5 pounds; as per ADAABAG Section 404.2.9: 36" x 84" Aluminum, Store Front, with Push Bar, Deadbolt and Door Handle, Factory Finish, Exterior Entrance Door, Double door with self-closing hardware. Located on South side of building, (2) located at the gift shop entry and (2) located at the grocery store entry. | 2027
82668 |  | (CN) CBV-001 Grocery Store/Gift Shop/Activities (CB-1) | LMAC | Adjust Door closer so that the maximum force to pull or push open the door is a maximum of 5 pounds; as per ADAABAG Section 309.4.and 404.2.9; 36" x 80" Exterior Entrance Door, with kick plate and pull handle. Located at entrance to women’s and men’s restrooms on North end of building. | 2027
82668 |  | (CN) CBV-001 Grocery Store/Gift Shop/Activities (CB-1) | LMAC | Add pull handles on the interior of the stall doors as per ADAABAG Section 604.8.1.2; 404.2.7; 92" x 84" x 60" Fabricated Toilet Partition, 1 - 36" x58" door. Located in the men’s restroom | 2027
82668 |  | (CN) CBV-001 Grocery Store/Gift Shop/Activities (CB-1) | LMAC | Add self-closing hinge on stall doors as per ADAABAG Section 604.8.1.2; 92" x 84" x 60" Fabricated Toilet Partition, 1 - 36" x58" door. Located in the men’s restroom | 2027
82668 |  | (CN) CBV-001 Grocery Store/Gift Shop/Activities (CB-1) | LMAC | Relocate rear grab bar is positioned a minimum of 12" to the centerline of the toilet on one side and a minimum of 24" to the other side as per ADAABAG Section 605.5.2: 1-1/2" diameter Grab Bar, 36" long. One located behind the water closet in the men’s, and one located in the women’s restroom at handicap stall | 2027
82668 |  | (CN) CBV-001 Grocery Store/Gift Shop/Activities (CB-1) | LMAC | Add pull handles on the interior of the stall doors as per ADAABAG Section 604.8.1.2; 404.2.7; 168" x 84" x 60" Fabricated Toilet Partition, 1 - 36" x58" doors. Located in the women’s restroom | 2027
82668 |  | (CN) CBV-001 Grocery Store/Gift Shop/Activities (CB-1) | LMAC | Add self-closing hinge on stall doors as per ADAABAG Section 604.8.1.2; 168" x 84" x 60" Fabricated Toilet Partition, 1 - 36" x58" doors. Located in the women’s restroom | 2027
82668 |  | (CN) CBV-001 Grocery Store/Gift Shop/Activities (CB-1) | LMAC | Add handrail to other side of stairs so there will be one on each side as per ADAABAG Section 504.6, 505.2; Wood, Straight-Run Design, with Wood Railing, (15 LF) Stairs to upper storage and office | 2027
82668 |  | (CN) CBV-001 Grocery Store/Gift Shop/Activities (CB-1) | LMAC | Relocate flush control valve so that it is no higher than 44" above the floor, as per ADAABAG Section 605.4; Urinal, Located in men’s restroom | 2027
82668 |  | (CN) CBV-001 Grocery Store/Gift Shop/Activities (CB-1) | LMAC | Relocate flush control handle so that it is located on the open side of the water closet as per ADAABAG Section 604.6; Water Closet, Located in men’s restroom | 2027
82668 |  | (CN) CBV-001 Grocery Store/Gift Shop/Activities (CB-1) | LMCO | Remove obstructions in front of panel as per NEC Code Reference 110.26. 14" x 18" Metal Panel Box, Square D brand, with, 16 Breakers, 100 Amp/3 Wire System, Electrical Sub Panel Located in the attic along the north wall. | 2027
82668 |  | (CN) CBV-001 Grocery Store/Gift Shop/Activities (CB-1) | LMCO | Label properly the electrical panel L. as per NEC Reference Code 110.22; 22" x 34" Metal Panel Box, Square D brand, with, 30 Breakers, 225 Amp/3 Wire System, Electrical Sub Panel L. Located along the south wall of the grocery store in the southwest corner next to the doors that lead to receiving area. | 2027
82668 |  | (CN) CBV-001 Grocery Store/Gift Shop/Activities (CB-1) | LMCO | Replace missing cover on electrical panel as per NEC Code Reference 408.38. 32" x 64" Metal Panel Box, Square D brand, with, 10 Breakers, Electrical Sub Panel 800 hundred amp. Located along the west wall in the electrical room. | 2027
82668 |  | (CN) CBV-001 Grocery Store/Gift Shop/Activities (CB-1) | LMFS | Repair non-working emergency lights. 12" x 8" Wall Mounted, Emergency Exit Sign One located above the stair landing that leads to basement | 2027
82703 |  | (CN) CBV-004 Launderette/Showers (CB-3 CB Conc Laundry/Sh | CRDM | Replace as it is beyond its useful life; 58" x 30" Fiberglass, Shower Surround Insert, includes shower pan with a 4-inch drain. Located in the accessible stalls in the men's and women's showers. | 2027
82703 |  | (CN) CBV-004 Launderette/Showers (CB-3 CB Conc Laundry/Sh | CRDM | Replace as it is beyond its useful life; Metal, Mixing Valve - Shower, Located in the men’s and women’s showers | 2027
82703 |  | (CN) CBV-004 Launderette/Showers (CB-3 CB Conc Laundry/Sh | CRDM | Replace emergency lights in the boiler room with functional lights. Wall Mounted, with dual emergency lights, Emergency Exit Sign Located in the boiler room on the west wall above doorway. | 2027
82703 |  | (CN) CBV-004 Launderette/Showers (CB-3 CB Conc Laundry/Sh | CRDM | Replace as it is beyond its useful life; Wall Mounted, with dual emergency lights, Emergency Exit Sign, Located in the generator room along the east wall | 2027
82703 |  | (CN) CBV-004 Launderette/Showers (CB-3 CB Conc Laundry/Sh | DM | Fill rodent holes at structure foundation perimeter | 2027
82703 |  | (CN) CBV-004 Launderette/Showers (CB-3 CB Conc Laundry/Sh | DM | Replace window gaskets as they are passed end of useful life. | 2027
82703 |  | (CN) CBV-004 Launderette/Showers (CB-3 CB Conc Laundry/Sh | DM | Replace baseboard tile around Wi-Fi area (6 LF). 12" x 6" Tile - Ceramic, Baseboard Trim. | 2027
82703 |  | (CN) CBV-004 Launderette/Showers (CB-3 CB Conc Laundry/Sh | DM | Test for suspected mold then remediate as required; Located under windows in women's shower area. Drywall, Painted, Interior Wall Covering Material, | 2027
82703 |  | (CN) CBV-004 Launderette/Showers (CB-3 CB Conc Laundry/Sh | DM | Add screen to vent at end of duct to prevent rodents and birds from entering | 2027
82703 |  | (CN) CBV-004 Launderette/Showers (CB-3 CB Conc Laundry/Sh | LMAC | Adjust door closer so that from an open position of 90 degrees, the door will take at least 5 seconds to move to a point 12degrees from the latch, measured to the leading edge of the door; as per ADAABAG Section 404.2.8.1 Also, adjust the closer so the force required to push or pull open the door is a maximum of 5 lbs.; as per ADAABAG Section 404.2.9. 68" x 88" Glazed Store Front Door, With 24 x 70“ window, double door, with panic hardware. Located at main entry | 2027
82703 |  | (CN) CBV-004 Launderette/Showers (CB-3 CB Conc Laundry/Sh | LMAC | Add spring hinge to accessible stall door so that it will be serf closing as per ADAABAG Section 604.8.1.2 and add pull hardware to both sides of the accessible stall door, as per ADAABAG Section 604.8.1.2, 404.2.7; 98" x 72" x 63" Solid Surface, Fabricated Toilet Partition, With 1- 34"x56" door. Located in the men’s restroom. | 2027
82703 |  | (CN) CBV-004 Launderette/Showers (CB-3 CB Conc Laundry/Sh | LMAC | Add spring hinge to accessible stall door so that it will be serf closing as per ADAABAG Section 604.8.1.2 and add pull hardware to both sides of the accessible stall door, as per ADAABAG Section 604.8.1.2, 404.2.7; 11'-5" x 70" x 64" Fabricated Toilet Partition, With 1- 34"x56" door. And 2 - (24"x56" doors,) Located in the women’s restroom. | 2027
82703 |  | (CN) CBV-004 Launderette/Showers (CB-3 CB Conc Laundry/Sh | LMAC | Adjust height of the grab bar in the men's accessible toilet stall to be between 33"-36" from the floor surface as per ADAABAG Section 609.4; 1 -1/2" diameter Stainless Steel, Grab Bar, 24" long. | 2027
82703 |  | (CN) CBV-004 Launderette/Showers (CB-3 CB Conc Laundry/Sh | LMAC | Replace rear grab bars located on the rear wall of the accessible stalls in the men's and women's restroom/shower to be a minimum of 36" long as per ADAABAG Section 604.5.2 and make sure the grab bar is positioned a minimum of 12" to the centerline of the toilet on one side and a minimum of 24" to the other side as per ADAABAG Section 604.5.2; 1-1/2" diameter Stainless Steel, Grab Bar, 24" long. | 2027
82703 |  | (CN) CBV-004 Launderette/Showers (CB-3 CB Conc Laundry/Sh | LMAC | Replace Side wall grab bars located in the men's and women's restroom/shower to be a minimum of 42" long as per ADAABAG Section 604.5.1 and make sure the distance on the side wall begins 12" or less from the corner of the wall, as per ADAABAG Section 604.5.1; 1-1/2" diameter Stainless Steel, Grab Bar, 24" long. | 2027
82703 |  | (CN) CBV-004 Launderette/Showers (CB-3 CB Conc Laundry/Sh | LMAC | Adjust urinal height so the rim is a maximum of 17" above the floor as per ADAABAG Section 605.2; Porcelain, Tankless, Wall Mounted, with Manual Handle Flush Valve, Urinal, Located in the men’s showers | 2027
82703 |  | (CN) CBV-004 Launderette/Showers (CB-3 CB Conc Laundry/Sh | LMAC | Adjust lavatory height so the rom or counter surface is no higher than 34" above the finished floor, as per ADAABAG Section F213.3.4 and 606.3; 60" x 22" Solid Surface, Drop-in-Countertop, Wall Mounted, Lavatory, with two drop-in sinks, which are oval shapes sized 16" x 14". Located in the men’s showers | 2027
82703 |  | (CN) CBV-004 Launderette/Showers (CB-3 CB Conc Laundry/Sh | LMAC | Add protecting covering for the hot water and drainpipes under the accessible lavatory/sink in the men's and women's rest rooms as per ADAABAG Section 606.5; 60" x 22" Solid Surface, Drop-in-Countertop, Wall Mounted, Lavatory, with two drop-in sinks, which are oval shapes sized 16" x 14". Located in the men’s showers | 2027
82703 |  | (CN) CBV-004 Launderette/Showers (CB-3 CB Conc Laundry/Sh | LMAC | Adjust lavatory height so the rom or counter surface is no higher than 34" above the finished floor, as per ADAABAG Section F213.3.4 and 606.3; 82" x 22" Solid Surface, Drop-in-Countertop, Wall Mounted, Lavatory, with three drop-in sinks, which are oval shapes sized 16" x 14". ln the women's showers. | 2027
82703 |  | (CN) CBV-004 Launderette/Showers (CB-3 CB Conc Laundry/Sh | LMAC | Add protecting covering for the hot water and drainpipes under the accessible lavatory/sink in the men's and women's rest rooms as per ADAABAG Section 606.5; 82" x 22" Solid Surface, Drop-in-Countertop, Wall Mounted, Lavatory, with three drop-in sinks, which are oval shapes sized 16" x 14". ln the women's showers. | 2027
82703 |  | (CN) CBV-004 Launderette/Showers (CB-3 CB Conc Laundry/Sh | LMCO | Install lever on door to properly close electrical panel to ensure safety as per NEC Code Reference 408.38. 22" x 50" Metal Panel Box, General Electric brand, with, 20 Breakers, 400 Amp/3 Wire System, Electrical Sub Panel Located along the south wall of the boiler room in the southwest corner. | 2027
82703 |  | (CN) CBV-004 Launderette/Showers (CB-3 CB Conc Laundry/Sh | LMCO | Replace missing outlet cover on the outlet located behind the reception desk in the northeast corner as per NEC Code Reference 406.5 (F). Ungrounded, 2-Wire Receptacle Located throughout the building. | 2027
82703 |  | (CN) CBV-004 Launderette/Showers (CB-3 CB Conc Laundry/Sh | LMFS | Replace emergency lights with updated electrical emergency lights/signage. Wall Mounted, with dual emergency lights, Emergency Exit Sign Located in the generator room along the east wall. | 2027
82703 |  | (CN) CBV-004 Launderette/Showers (CB-3 CB Conc Laundry/Sh | RMDM | Repaint siding at dryer vents on roof. T-111, Painted, Exterior Siding Material, Located at dryer vents on roof. (53 LF) | 2027
82703 |  | (CN) CBV-004 Launderette/Showers (CB-3 CB Conc Laundry/Sh | RMDM | Repaint interior wall covering located in the mechanical room. Drywall, Painted, Interior Wall Covering Material, 1/2" thick double layer, painted. Located in the mechanical rooms, 111LF. | 2027
82703 |  | (CN) CBV-004 Launderette/Showers (CB-3 CB Conc Laundry/Sh | RMDM | Repaint ceiling in the mechanical room as it is beyond its useful life | 2027
82706 |  | (CN) CBV-015 Telephone Equipment/Storage (CB-4) | DM | Repair hanging soffit and missing ventilation in soffit located on both sides of building. 16" Plywood Sheeting, Painted, Soffit Covering With 2-inch continuous venting on both sides. | 2027
82707 |  | (CN) CBV-008 Marina Building (CB-5) | CRDM | Replace as it is beyond its useful life; 26" x 38" Through the Wall, Evaporative Cooler, Set upstairs in the attic/storage area. Evaporator cooler has a quarter inch waterline attached to it and sits in a pan to collect excess water. | 2027
82707 |  | (CN) CBV-008 Marina Building (CB-5) | CRDM | Replace as it is beyond its useful life; 9" x 12" Electric Wall Heater, Located on west wall in the bathroom | 2027
82707 |  | (CN) CBV-008 Marina Building (CB-5) | CRDM | Replace as it is beyond its useful life; 4" diameter Dual Bulb, Exterior Light Fixture, Cover. Located on the south wall just east of the main entry on the south side right next to the patio stairs | 2027
82707 |  | (CN) CBV-008 Marina Building (CB-5) | DM | Repair faux stone footings around base of porch. | 2027
82707 |  | (CN) CBV-008 Marina Building (CB-5) | LMAC | Replace thresholds with one that has a maximum of 1/2" from the floor as per ADAABAG Section 404.2.5; 36" x 84" Exterior Entrance Door, With 21“ x 32“ upper lite and 21“ x 24“ lower lite. Located all entrances to main portion of structure (north, south, and west sides) | 2027
82707 |  | (CN) CBV-008 Marina Building (CB-5) | LMAC | Adjust self-closer so that from an opening position of 90 degrees, the door will take at least 5 seconds to move to a point 12 degrees from the latch, measured to the leading edge of the door; 36" x 84" Exterior Entrance Door, With 21“ x 32“ upper lite and 21“ x 24“ lower lite. Located all entrances to main portion of structure (north, south, and west sides) | 2027
82707 |  | (CN) CBV-008 Marina Building (CB-5) | LMAC | Replace door hardware with one that does not require tight grasping, pinching, or twisting of the wrist to operate as per ADAABAG Section 309.4; 42" x 80" Hollow Core - Wood, Standard Interior Door, standard twist knob, located from Corridor to storage room | 2027
82707 |  | (CN) CBV-008 Marina Building (CB-5) | LMAC | Replace door hardware with one that does not require tight grasping, pinching, or twisting of the wrist to operate as per ADAABAG Section 309.4; 30" x 80" Hollow Core - Wood, Standard Interior Door, style hardware with Key lock set. Located from corridor to managers office. | 2027
82707 |  | (CN) CBV-008 Marina Building (CB-5) | LMAC | Adjust height of the spout outlet so that it is no higher than 30" from the floor as per ADAABAG Section 602.4; 12" diameter Stainless Steel, Single Basin, Drinking Fountain, Exterior. Located west of the main entry on the south end | 2027
82708 |  | (CN) CBV-002 Chuckwagon/CBV-002 Chuckwgn/Cafe Ct (CB-6 John | CRDM | Replace as it is beyond its useful life; 12" diameter Through the Wall, Whole Room Exhaust Fan, Located beside EDR emergency exit. | 2027
82708 |  | (CN) CBV-002 Chuckwagon/CBV-002 Chuckwgn/Cafe Ct (CB-6 John | CRDM | Replace as it is beyond its useful life; Push Reset, GFCI Protected Receptacle, one located along the west exterior wall near the northwest corner of the restaurant. One located on the west exterior wall of the cafe foyer near the entry doors. | 2027
82708 |  | (CN) CBV-002 Chuckwagon/CBV-002 Chuckwgn/Cafe Ct (CB-6 John | CRDM | Replace 6" diameter Ceiling Mounted, Emergency Lighting, Single emergency light. Located in the men’s and women’s public restrooms. | 2027
82708 |  | (CN) CBV-002 Chuckwagon/CBV-002 Chuckwgn/Cafe Ct (CB-6 John | CRDM | Replace as it is beyond its useful life; 20" x 41" Metal Panel Box, Square D brand, with, 38 Breakers, 225 Amp/3 Wire System, Electrical Sub Panel, Located in the EDR along the north wall next to the dishwashing area. | 2027
82708 |  | (CN) CBV-002 Chuckwagon/CBV-002 Chuckwgn/Cafe Ct (CB-6 John | CRDM | Replace as it is beyond its useful life; Wall Mounted, Fire Alarm with Bell, located above the doors that lead to the boiler room. | 2027
82708 |  | (CN) CBV-002 Chuckwagon/CBV-002 Chuckwgn/Cafe Ct (CB-6 John | DM | Replace missing gravel to roof in areas where it is exposed. Approximately 5%. Built - up, Roof Finish, Tar and gravel. Located over the entire building. | 2027
82708 |  | (CN) CBV-002 Chuckwagon/CBV-002 Chuckwgn/Cafe Ct (CB-6 John | DM | Secure ventilator Self Contained, Enclosed, Roof Top Package Unit, Dayton, Model number 4hx98b, centrifugal roof/wall ventilator belt drive, Located above cafe area on the roof. | 2027
82708 |  | (CN) CBV-002 Chuckwagon/CBV-002 Chuckwgn/Cafe Ct (CB-6 John | LMAC | Adjust self-closer so that from an opening position of 90 degrees, the door will take at least 5 seconds to move to a point 12 degrees from the latch, measured to the leading edge of the door; Per ADAABAG Section 404.2.8.1; 36" x 84" Exterior Entrance Door, Exit storefront door with glazing at the south-west and north-east facades of the cafe dining room; and the north and west facades of the restaurant. | 2027
82708 |  | (CN) CBV-002 Chuckwagon/CBV-002 Chuckwgn/Cafe Ct (CB-6 John | LMAC | Adjust self-closer so that from an opening position of 90 degrees, the door will take at least 5 seconds to move to a point 12 degrees from the latch, measured to the leading edge of the door; Per ADAABAG Section 404.2.8.1; 72" x 84" Exterior Entrance Door, Door with pull handle and crash bar. Double door to café foyer. | 2027
82708 |  | (CN) CBV-002 Chuckwagon/CBV-002 Chuckwgn/Cafe Ct (CB-6 John | LMAC | Adjust self-closer so that from an opening position of 90 degrees, the door will take at least 5 seconds to move to a point 12 degrees from the latch, measured to the leading edge of the door; Per ADAABAG Section 404.2.8.1; 36" x 80" Exterior Entrance Door, 24"x30" light. Located on the west and east walls of EDR. (This component is part of the historic fabric of the building) | 2027
82708 |  | (CN) CBV-002 Chuckwagon/CBV-002 Chuckwgn/Cafe Ct (CB-6 John | LMAC | Add self-closing hinge on stall doors as per ADAABAG Section 604.8.1.2; 98" x 60" x 58" Fabricated Toilet Partition, With 1- 24"x58" door and 1 - 36"x58" door. Located in the men’s public restroom | 2027
82708 |  | (CN) CBV-002 Chuckwagon/CBV-002 Chuckwgn/Cafe Ct (CB-6 John | LMAC | Add pull handles on the interior of the stall doors as per ADAABAG Section 604.8.1.2; 404.2.7; 98" x 60" x 58" Fabricated Toilet Partition, With 1- 24"x58" door and 1 - 36"x58" door. Located in the men’s public restroom | 2027
82708 |  | (CN) CBV-002 Chuckwagon/CBV-002 Chuckwgn/Cafe Ct (CB-6 John | LMAC | Add self-closing hinge on stall doors as per ADAABAG Section 604.8.1.2; 165" x 84" x 60" Fabricated Toilet Partition, Stainless steel with 3- 24"x 58" doors and 1- 36"x58" door. Located in the women’s public restroom | 2027
82708 |  | (CN) CBV-002 Chuckwagon/CBV-002 Chuckwgn/Cafe Ct (CB-6 John | LMAC | Add pull handles on the interior of the stall doors as per ADAABAG Section 604.8.1.2; 404.2.7; 165" x 84" x 60" Fabricated Toilet Partition, Stainless steel with 3- 24"x 58" doors and 1- 36"x58" door. Located in the women’s public restroom | 2027
82708 |  | (CN) CBV-002 Chuckwagon/CBV-002 Chuckwgn/Cafe Ct (CB-6 John | LMAC | Relocate flush control handle so that it is located on the open side of the water closet as per ADAABAG Section 604.6; Water Closet, located in accessible stalls in the men's and women's restroom. | 2027
82708 |  | (CN) CBV-002 Chuckwagon/CBV-002 Chuckwgn/Cafe Ct (CB-6 John | LMAC | Relocate flush control valve so that it is no higher than 44" above the floor, as per ADAABAG Section 605.4; Urinal, located in the men's public restroom. | 2027
82708 |  | (CN) CBV-002 Chuckwagon/CBV-002 Chuckwgn/Cafe Ct (CB-6 John | LMAC | Add protecting covering for the hot water and drainpipes under the accessible lavatory/sink in the men's and women's rest rooms as per ADAABAG Section 606.5; 16" Lavatory, located in the men's and women's public restrooms. | 2027
82710 |  | (CN) CBV-100 Cabin Office (CB-7 Cabin Rental Office) | CRDM | Replace as it is past its useful life; 1" x 1" Wood, Painted, Door & Window Trim, (95 LF) Located on all Windows and doors | 2027
82710 |  | (CN) CBV-100 Cabin Office (CB-7 Cabin Rental Office) | CRDM | Replace as it is past its useful life; 6" x 6" Chrome Finish, Faucet - Single Valve, located on wall hung sink in bathroom | 2027
82710 |  | (CN) CBV-100 Cabin Office (CB-7 Cabin Rental Office) | CRDM | Replace as it is past its useful life; 16" x 9" Electric Wall Heater, Electric wall heater is a Raywall. Located on the north wall assistant managers office | 2027
82710 |  | (CN) CBV-100 Cabin Office (CB-7 Cabin Rental Office) | CRDM | Replace as it is past its useful life; 16" x 24" Electric Wall Heater, Located along the south wall the receptionist area. | 2027
82710 |  | (CN) CBV-100 Cabin Office (CB-7 Cabin Rental Office) | CRDM | Replace as it is past its useful life; 20" x 6" Metal, Single Bulb, Bar Light, each light has one rocker switch. Located underneath built-in desk right underneath historic mailboxes. | 2027
82710 |  | (CN) CBV-100 Cabin Office (CB-7 Cabin Rental Office) | CRDM | Replace as it is past its useful life; 4" x 7" with glass cover, Exterior Light Fixture, Located above the exterior door on the east and west end in the northeast corner and the northwest corner | 2027
82710 |  | (CN) CBV-100 Cabin Office (CB-7 Cabin Rental Office) | LMAC | Replace door lockset with on that does not require tight grasping, tight pinching or twisting of the wrist to operate as per ADAABAG Section 309.4; 31.5" x 73" Exterior Entrance Door, 4 panels, built-up door with 1"x6" and 1"x10" rough sawn members. Located all exterior doors | 2027
82710 |  | (CN) CBV-100 Cabin Office (CB-7 Cabin Rental Office) | LMAC | Add Kick plates to provide the necessary 10" smooth surface extending the full width of the bottom of the push side of the door as per ADAABAG Section 404.2.10: 31.5" x 73" Exterior Entrance Door, 4 panels, built-up door with 1"x6" and 1"x10" rough sawn members. Located all exterior doors | 2027
82710 |  | (CN) CBV-100 Cabin Office (CB-7 Cabin Rental Office) | LMAC | Adjust spring hinge so that from an open position of 70 degrees the door will take at least 1.5 seconds to close, as per ADAABAG Section 404.2.8.2; 32" x 72" Exterior Entrance Door, Screen door, 1x solid wood frame, metal screen. located at all exterior entrances. | 2027
82710 |  | (CN) CBV-100 Cabin Office (CB-7 Cabin Rental Office) | LMAC | Replace door lockset with on that does not require tight grasping, tight pinching or twisting of the wrist to operate as per ADAABAG Section 309.4; 28" x 78" Standard Interior Door, Interior panel door with five panels. Basic lock set hardware. Doors located on the north wall of the general manager’s office one door leading to the bathroom the other door leading to the office | 2027
82710 |  | (CN) CBV-100 Cabin Office (CB-7 Cabin Rental Office) | LMAC | Adjust spring hinge so that from an open position of 70 degrees the door will take at least 1.5 seconds to close, as per ADAABAG Section 404.2.8.2; 28" x 78" Standard Interior Door, Interior panel door with five panels. Basic lock set hardware. Doors located between the lobby and back office. | 2027
82710 |  | (CN) CBV-100 Cabin Office (CB-7 Cabin Rental Office) | LMAC | Add Kick plates to provide the necessary 10" smooth surface extending the full width of the bottom of the push side of the door as per ADAABAG Section 404.2: 28" x 78" Standard Interior Door, Interior panel door with five panels. Basic lock set hardware. Doors located to managers office from lobby. | 2027
82710 |  | (CN) CBV-100 Cabin Office (CB-7 Cabin Rental Office) | LMAC | Replace door lockset with on that does not require tight grasping, tight pinching or twisting of the wrist to operate as per ADAABAG Section 309.4; 28" x 78" Standard Interior Door, Hollow wood door. Door is a flat slab door and has a normal knob style doorknob | 2027
82710 |  | (CN) CBV-100 Cabin Office (CB-7 Cabin Rental Office) | LMAC | Replace door lockset with on that does not require tight grasping, tight pinching or twisting of the wrist to operate as per ADAABAG Section 309.4; 32" x 74" Standard Interior Door, Door is a panel door with four panels. Door is also stained and has a knob style doorknob. Located north wall of the office | 2027
82710 |  | (CN) CBV-100 Cabin Office (CB-7 Cabin Rental Office) | LMAC | Add protecting covering for the hot water and drainpipes under the accessible lavatory/sink in the rest room as per ADAABAG Section 606.5; 20" x 20" Lavatory, Located in the bathroom along the west. Wall. | 2027
82710 |  | (CN) CBV-100 Cabin Office (CB-7 Cabin Rental Office) | LMAC | Replace water closet with one that the height is between 17" to 19" when measured from the floor to the top of the toilet seat and that the flush control valve is on the open side of the water closet, as per ADAABAG Sections 604.4 & 604.6; Water Closet, Located in the bathroom along the west wall. | 2027
82710 |  | (CN) CBV-100 Cabin Office (CB-7 Cabin Rental Office) | LMAC | Replace bathroom faucet with one that is easy to operate with one hand and not require tight grasping, pinching, or twisting of the wrist, per ADAABAG Section 606.4, 309; 6" x 6" Faucet - Single Valve, located on wall hung sink in bathroom. | 2027
82711 |  | (CN) CBV-194 Cabin 2 (CB-8 COLTER BAY Concessions | RMDM | Refinish exterior log as they are past due; 8" diameter Stacked Log, Exterior Wall Frame Assembly, with Mortise and Tenon, and Chinking mortar fill Located all exterior walls. (72 LF) | 2027
82712 |  | (CN) CBV-195 Cabin 4 (CB-9 CB Concessions Cabin 4) | RMDM | Refinish exterior logs as they are past due; 8" diameter Stacked Log, Exterior Wall Frame Assembly, with Mortise and Tenon, and Chinking mortar fill Located all exterior walls. (72 LF) | 2027
82715 |  | (CN) CBV-197 Cabin 10 & 12 (CB-11 CB Concessions C | DM | Replace missing gravel on the roof approximately 30%; Tar & Gravel, Roof Finish, with felt paper underlayment, with 4" metal drip edge Located over the entire structure. | 2027
82715 |  | (CN) CBV-197 Cabin 10 & 12 (CB-11 CB Concessions C | LMCO | Replace missing smoke detector in entryway as per code IBC Sections 907.2.11.1 & 907.2.11.2, 5" diameter Battery Operated, Smoke Detector Located in both bedrooms and in entryway. | 2027
82716 |  | (CN) CBV-198 Cabin 14 & 16 (CB-12 CB Concessions C | DM | Replace wood planking on the exterior side as multiple planks are deteriorating and have water damage. (158 SF); 8" to 10" Rafters - Log Timber, Pitched Roof Construction, @ 36 O.C. 8" to 10" logs (150 LF) with 1"x12" wood planking (637 SF). Located above the entire structure. | 2027
82716 |  | (CN) CBV-198 Cabin 14 & 16 (CB-12 CB Concessions C | RMDM | Refinish exterior log walls as it is past due; Stacked Log, Exterior Wall Frame Assembly, with Mortise and Tenon, and Chinking mortar fill 6" to 8" logs (89 LF). Located around the entire structure, (except south exterior wall of both bathrooms). | 2027
82720 |  | (CN) CBV-106 Cabin 201 & 203 (CB-14 CB Concessions Cabin) | RMDM | Refinish exterior log walls as they are past due; Stacked Log, Exterior Wall Frame Assembly, with Mortise and Tenon, and Chinking mortar fill 6" to 8" logs Located around the entire building except at bathrooms | 2027
82721 |  | (CN) CBV-102 Cabin 202 & 204 (CB-15 CB Concessions Cabin) | RMDM | Refinish exterior logs as they are past due; Stacked Log, Exterior Wall Frame Assembly, and Chinking mortar fill 8" logs corner vertical posts (located at the north-west and south-west corners of the building) (114 LF). | 2027
82724 |  | (CN) CBV-103 Cabin 206 (CB-16 CB Concessions Cabin) | RMDM | Refinish exterior log siding as it is past due, Wood, Exterior Siding Material, Painted 8" wide quarter log siding, located the exterior of the bathroom build out. | 2027
82725 |  | (CN) CBV-104 Cabin 210 (CB-17 CB Concessions Cabin 210) | DM | Refinish exterior siding as it is past due; 1" x 6" Wood, Exterior Siding Material located around bathroom and storage area. | 2027
82725 |  | (CN) CBV-104 Cabin 210 (CB-17 CB Concessions Cabin 210) | RMDM | Refinish exterior log walls as they are past due; 8" diameter Stacked Log, Exterior Wall Frame Assembly, and Chinking mortar fill Located around the entire exterior of the building except for the closet and the exterior side of the bathroom. (75 LF) | 2027
82726 |  | (CN) CBV-105 Cabin 212 (CB-18 Cabin 212) | DM | Repair concrete where exposed rebar on the second edge. Concrete, Thickened Edge Slab on Grade, 6 Thick 16“ x 36“ drop off edge. Located underneath entire structure. (602 SF) | 2027
82726 |  | (CN) CBV-105 Cabin 212 (CB-18 Cabin 212) | RMDM | Refinish exterior logs as they are past due. Stacked Log, Exterior Wall Frame Assembly, and Chinking mortar fill with wood chinking on the exterior (78 LF). Located on all exterior walls except the east wall where we have a storefront system. | 2027
82728 |  | (CN) CBV-107 Cabin 205 & 207 (CB-19 Cabin) | LMCO | Provide 30-inch clear floor space in front of electrical panel as per NEC Code Reference 110.26, 20" x 26" Metal Panel Box, Main Electrical Service Panel, General Electric brand, with, 12 Breakers, 100 Amp/3 Wire System Located in bedroom of 207. | 2027
82728 |  | (CN) CBV-107 Cabin 205 & 207 (CB-19 Cabin) | RMDM | Refinish exterior logs as their past time; Stacked Log, Exterior Wall Frame Assembly, with Mortise and Tenon, and Chinking mortar fill 6" to 8" logs Located around the entire building except at bathrooms | 2027
82729 |  | (CN) CBV-108 Cabin 209 & 211 (CB-20 Cabin) | DM | Refinish Exterior Log walls as they are past due; Stacked Log, Exterior Wall Frame Assembly, with Mortise and Tenon, and Chinking mortar fill 6" to 8" logs Located around the entire building except at bathrooms | 2027
82729 |  | (CN) CBV-108 Cabin 209 & 211 (CB-20 Cabin) | DM | Provide required clear space in front of electrical panel as per the NEC (National Electrical Code) Reference 110.26; 20" x 26" Metal Panel Box, Main Electrical Service Panel, General Electric brand, with, 12 Breakers, 100 Amp/3 Wire System Located in bedroom of 211 | 2027
82730 |  | (CN) CBV-109 Cabin 213, 215 (CB-21 Cabin) | RMDM | Refinish exterior log walls as they are past due; 8" diameter Stacked Log, Exterior Wall Frame Assembly, with Mortise and Tenon, and Chinking mortar fill Located all exterior walls. | 2027
82731 |  | (CN) CBV-110 Cabin 219, 221, 223, 225 & 227 (CB-22 Cabin) | RMDM | Refinish women's restroom door as it is past due; 30" x 76" Wood, Exterior Entrance Door, Lockset with Key, Painted Five panel door. Located in each unit and both men’s and women’s bathrooms. Bedroom doors also have deadbolts. | 2027
82732 |  | (CN) CBV-112 Cabin 229 (CB-23 Cabin 229) | LMCO | Add smoke detector in storage room as per IBC Code Sections 907.2.11.1 & 907.2.11.2, 6" diameter Battery Operated, Needed in the storage area. | 2027
82733 |  | (CN) CBV-113 Cabin 231 & 233 (CB-24 Cabin) | DM | Refinish exterior log walls as they are past due; Stacked Log, Exterior Wall Frame Assembly, with Mortise and Tenon, and Chinking mortar fill 6" to 8" logs located around the entire building except at bathrooms | 2027
82733 |  | (CN) CBV-113 Cabin 231 & 233 (CB-24 Cabin) | DM | Provide required clearance of a minimum of 30" in front of the electrical panel as per the NEC (National Electrical Code) 110.26; 20" x 26" Metal Panel Box, Main Electrical Service Panel, General Electric brand, with, 12 Breakers, 100 Amp/3 Wire System Located in bedroom of 233. | 2027
82734 |  | (CN) CBV-114 Cabin 235, 237 (CB-25 Cabin) | RMDM | Refinish exterior log walls as they are past due. 8" diameter Stacked Log, Exterior Wall Frame Assembly, with Mortise and Tenon, and Chinking mortar fill Located all exterior walls. | 2027
82735 |  | (CN) CBV-131/132 Cabin 401 & 403 & 405 (CB-26/27 Cabin) | DM | Replace missing door to the bedroom of cabin 401; 28" x 80" Wood, Standard Interior Door, five panel door, Lockset Hardware, Painted. | 2027
82735 |  | (CN) CBV-131/132 Cabin 401 & 403 & 405 (CB-26/27 Cabin) | LMCO | Provide required clear space around electrical panel per NEC Code Reference 110.26 (minimum of 30" x 36"); 21" x 27" Metal Panel Box, Main Electrical Service Panel, General Electric brand, with, 16 Breakers, 100 Amp/3 Wire System Located in cabin 405 in the entry way. | 2027
82738 |  | (CN) CBV-115 Cabin 402, 404, 408, 412 & 414 (CB-29 Cabin) | RMDM | Refinish exterior log walls as they are past due; Stacked Log, and Chinking mortar fill, Exterior Wall Frame Assembly, 8" logs (275 LF), 2x6 framed in fill with 4" vertical siding at removed doors and windows (26 SF). On north and south elevations. | 2027
82739 |  | (CN) CBV-116 Cabin 416 & 418 (CB-30 Cabin) | DM | Refinish exterior log walls as they are past due; Stacked Log, Exterior Wall Frame Assembly, with Mortise and Tenon, and Chinking mortar fill 6" to 10" logs. Located all exterior walls (note that each cabin has four walls). | 2027
82740 |  | (CN) CBV-134 Cabin 417 & 419 (CB-31 Cabin) | DM | Refinish exterior log walls as they are past due; Stacked Log, Exterior Wall Frame Assembly, with Mortise and Tenon, and Chinking mortar fill 6" to 10" logs. Located all exterior walls (note that each cabin has four walls). | 2027
82741 |  | (CN) CBV-117 Cabin 420 & 422 (CB-32 Cabin) | LMCO | Provide proper clearance for electrical panel by permanently removing dresser as per NEC Code Reference 110.26, Metal Panel Box, Painted, Electrical Sub Panel, 10 Breakers, 125 Amp/3 Wire System Trumbull Electric, 10 breakers. Located in South bedroom | 2027
82742 |  | (CN) CBV-135 Cabin 421 (CB-33 Cabin 421) | LMCO | Provide 30-inch clearance space in front of electrical panel as per the NEC code Reference 110.26; 20" x 25" Metal Panel Box, Main Electrical Service Panel, General Electric brand, with, 6 Breakers, 100 Amp/3 Wire System Located in the bedroom | 2027
82742 |  | (CN) CBV-135 Cabin 421 (CB-33 Cabin 421) | RMDM | Refinish exterior logs as they are past due; Stacked Log, Exterior Wall Frame Assembly, with Mortise and Tenon, and Chinking mortar fill 6" to 8" logs. Located all exterior walls except around front entry. (77 LF) | 2027
82743 |  | (CN) CBV-136 Cabin 423 (CB-34 Cabin 423) | RMDM | Refinish exterior logs as they are past due; Stacked Log, Exterior Wall Frame Assembly, with Mortise and Tenon, and Chinking mortar fill 6" to 8" logs. Located all exterior walls except around front entry. (77 LF) | 2027
82745 |  | (CN) CBV-137 Cabin 425 (CB-35 Cabin 425) | LMCO | Provide required clear space in front of electrical panel as per NEC Code Reference 110.26 (Minimum of 30" x 36") 20" x 26" Metal Panel Box, Main Electrical Service Panel, 6 Breakers, 100 Amp/3 Wire System Trimble Electric. Located in the bedroom | 2027
82745 |  | (CN) CBV-137 Cabin 425 (CB-35 Cabin 425) | RMDM | Refinish exterior log walls as they are past due; Stacked Log, Exterior Wall Frame Assembly, with Mortise and Tenon, and Chinking mortar fill 8" to 10" logs. Located at all exterior walls. (76 LF) | 2027
82748 |  | (CN) CBV-138 Cabin 427 & 429 (CB-37 Cabin) | RMDM | Refinish exterior log walls as they are past due; Stacked Log, Exterior Wall Frame Assembly, with Mortise and Tenon, and Chinking mortar fill 6" to 10" logs. Located all exterior walls (note that each cabin has four walls). | 2027
82749 |  | (CN) CBV-139 Cabin 431 (CB-38 Cabin) | LMCO | Add missing smoke detector in entryway as per IBC Code Sections 907.2.11.1 & 907.2.11.2, 6" Battery Operated, Smoke Detector Located in entry way. | 2027
82749 |  | (CN) CBV-139 Cabin 431 (CB-38 Cabin) | RMDM | Refinish exterior long as they are past due. 6" to 8" logs with 6" diameter corner posts and 6"x6" sill board. All exterior walls (107 LF) | 2027
82750 |  | (CN) CBV-119 Cabin 432 & 434 (CB-39 Cabin) | DM | Replace missing fascia board on the west side of the building (the whole length of cabin 432). (61 LF), 2" x 4" Wood, Fascia Board Laid horizontally painted. Located on the north and south sides of the building. | 2027
82750 |  | (CN) CBV-119 Cabin 432 & 434 (CB-39 Cabin) | RMDM | Refinish exterior logs as they are past due; Stacked Log, Exterior Wall Frame Assembly, with Mortise and Tenon, and Chinking mortar fill 6" to 10" logs. Located all exterior walls (note that each cabin has four walls). | 2027
82751 |  | (CN) CBV-140/141 Cabin 435 & 439,441 (CB-40/42 Cabin) | LMCO | Provide required clear space in front of electrical panel as per NEC Code Reference 110.26 (Minimum of 30" x 36"); 21" x 27" Metal Panel Box, Main Electrical Service Panel, General Electric brand, with, 16 Breakers, 100 Amp/3 Wire System Located in cabin 441 in the entry way. | 2027
82751 |  | (CN) CBV-140/141 Cabin 435 & 439,441 (CB-40/42 Cabin) | RMDM | Refinish exterior log walls as they are past due and in need of finishing; 8" diameter Stacked Log, Exterior Wall Frame Assembly, with Mortise and Tenon, and Chinking mortar fill Stained. Located all exterior walls except around bathrooms and at entry doors. | 2027
82752 |  | (CN) CBV-120 Cabin 436 & 438 (CB-41 Cabin) | LMCO | Provide 30-inch players face in front of electrical panel as per code 408.20, 20 " x 26" Metal Panel Box, Main Electrical Service Panel, 12 Breakers, 100 Amp/3 Wire System Trumbull Electric. Located in entry of cabin 438 | 2027
82754 |  | (CN) CBV-121 Cabin 440,442,444,446,448 & 450 (CB-43 Cabin) | LMCO | Add latch for electrical panel as per NEC Code Reference 408.38 Metal Panel Box, Main Electrical Service Panel, 34 Breakers, 150 Amp/3 Wire System Trumbull Electric. Located in cabin 440 | 2027
82755 |  | (CN) CBV-142 Cabin 443 (CB-44 Cabin) | RMDM | Refinish exterior logs as they are past due; Stacked Log, Exterior Wall Frame Assembly, with Mortise and Tenon, and Chinking mortar fill 6" to 8" logs with 6" diameter corner posts and 6"x6" sill board. All exterior walls (107 LF) | 2027
82756 |  | (CN) CBV-143 Cabin 447 (CB-45 Cabin) | RMDM | Refinish exterior logs as they are past due; Stacked Log, Exterior Wall Frame Assembly, with Mortise and Tenon, and Chinking mortar fill 6" to 8" logs with 6" diameter corner posts and 6"x6" sill board. All exterior walls (107 LF) | 2027
82757 |  | (CN) CBV-144/145 Cabin 451 & 455 (CB-46/48 Cabin) | LMCO | Replace missing smoke detector at entry way of cabin 451 as per IBC Code Sections 907.2.11.1 & 907.2.11.2 | 2027
82757 |  | (CN) CBV-144/145 Cabin 451 & 455 (CB-46/48 Cabin) | RMDM | Refinish exterior logs as they are past due; 8" diameter Stacked Log, Exterior Wall Frame Assembly, with Mortise and Tenon, and Chinking mortar fill and 1" fill on the inside. All exterior walls except walls around entry doors and around the bathrooms of both cabins and 6" diameter corner posts at each corner (59 LF). | 2027
82757 |  | (CN) CBV-144/145 Cabin 451 & 455 (CB-46/48 Cabin) | RMDM | Refinish siding as it is past due; 1" x 8" Wood, Exterior Siding Material, Painted Planks at front entries on the north side of the cabins (30 LF) and at bathrooms on the south side of the cabins (21 LF). | 2027
82758 |  | (CN) CBV-122 Cabin 454,456,458 & Guest Lounge (CB-47 Cabin) | DM | Replace the hardware of the entry door with accessible hardware, 32" x 80" Wood, Solid Core, Exterior Entrance Door, Round Handle, painted 5 panel, painted, Wood screen door with metal screen and closer. Located at main entry of lounge | 2027
82758 |  | (CN) CBV-122 Cabin 454,456,458 & Guest Lounge (CB-47 Cabin) | DM | Replace Handle Hardware at dining entry door to lounge with complaint accessible hardware.32" x 72" Wood, Solid Core, Exterior Entrance Door, Lockset with Key, painted 5 panel, painted. Located at dining. | 2027
82758 |  | (CN) CBV-122 Cabin 454,456,458 & Guest Lounge (CB-47 Cabin) | DM | Repair leaking pipe at hot water heater 20" diameter Electric, Water Heater - Residential, Rehem, 50 Gallon Located in closet off front room of guest lounge. Serial No. 0280121198, Model No. 666H-52D | 2027
82758 |  | (CN) CBV-122 Cabin 454,456,458 & Guest Lounge (CB-47 Cabin) | LMAC | Adjust the threshold that is at 1" high, so the raised threshold and floor level changes a maximum of 1/2" at accessible doors and beveled with a slope no greater than 1:2? as per code ADAABAG Section 404.2.5, Located at the main lounge entry. | 2027
82758 |  | (CN) CBV-122 Cabin 454,456,458 & Guest Lounge (CB-47 Cabin) | LMAC | Adjust door closer so that it closes at least 5 seconds from an open position of 90 degree, as per ADAABAG 404.2.8.1; 32" x 80" Wood, Screen Door, with Self-Closing Device, and with Handle, Painted Located at main entry of lounge | 2027
82758 |  | (CN) CBV-122 Cabin 454,456,458 & Guest Lounge (CB-47 Cabin) | LMAC | Replace handle hardware so that the handles, pulls, latches, locks, or other operating devices on doors have a shape that is easy to grasp with one hand and not require tight grasping, tight pinching or twisting of the wrist to operate as per code ADAABAG Section 309.4, 36" x 80" Wood, Solid Core, Exterior Entrance Door, Deadbolt and Door Handle, painted 5 panel, painted. Located at room #458 | 2027
82758 |  | (CN) CBV-122 Cabin 454,456,458 & Guest Lounge (CB-47 Cabin) | LMAC | Replace handle hardware so that the handles, pulls, latches, locks, or other operating devices on doors have a shape that is easy to grasp with one hand and not require tight grasping, tight pinching or twisting of the wrist to operate as per code ADAABAG Section 309.4, 28" x 75" Wood, Standard Interior Door, five panel door, Lockset Hardware, Painted Located at restroom. | 2027
82758 |  | (CN) CBV-122 Cabin 454,456,458 & Guest Lounge (CB-47 Cabin) | LMAC | Replace the doors hardware so that handles, pulls, latches, locks, or other operating devices on doors have a shape that is easy to grasp with one hand and not require tight grasping, tight pinching or twisting of the wrist to operate as per code ADAABAG Section 309.4 36" x 80" Wood, Standard Interior Door, five panel door, Standard Door Handle, Stained Located at bathrooms of unit 456 and 458 | 2027
82758 |  | (CN) CBV-122 Cabin 454,456,458 & Guest Lounge (CB-47 Cabin) | LMAC | Replace grab bars at the water closet to have a horizontal grab bar along the adjacent side wall that is at least 42" long and mounted 33"-36" above the floor for stabilization and assistance as per Department of Justice, ADAABAG 604.5.1, Located in the bathroom of unit 456 and 458. | 2027
82758 |  | (CN) CBV-122 Cabin 454,456,458 & Guest Lounge (CB-47 Cabin) | LMAC | Replace grab bars at the toilet in the water closet to have a horizontal grab bar along the wall behind the toilet that is at least 36" long and mounted 33"-36" above the floor for stabilization and assistance as per Department of Justice, ADAABAG 604.5.1, Located in the bathroom of unit 456 and 458. | 2027
82758 |  | (CN) CBV-122 Cabin 454,456,458 & Guest Lounge (CB-47 Cabin) | LMAC | Add protective covering to hot water and drainpipes on at least on sink, to protect against contact as per ADAABAG Section 606.5 located in the main bathroom. | 2027
82758 |  | (CN) CBV-122 Cabin 454,456,458 & Guest Lounge (CB-47 Cabin) | LMAC | Replace faucets so as can easily operable (i.e.: levers, wrist blades, single arm, etc.) and usable with one hand, without tight grasping, pinching, or twisting of the wrist as per ADAABAG Section 606.4,309, 6" Nickel Finish, Faucet - Single Valve (1) in room 458 (1) in room 456 and (1) in main restroom. | 2027
82758 |  | (CN) CBV-122 Cabin 454,456,458 & Guest Lounge (CB-47 Cabin) | LMAC | Replace the urinal that is 21" from rim so that the rim of the urinal is a maximum of 17" above the floor as per ADAABAG Section 605.2 14" x 19" Porcelain, Urinal, Tankless, Cut in Floor, with Manual Handle Flush Valve Located in restroom | 2027
82758 |  | (CN) CBV-122 Cabin 454,456,458 & Guest Lounge (CB-47 Cabin) | LMCO | Replace Door with shorter door to gain access to water heater, Guestroom 454, 21" x 80" Wood, Standard Interior Door, five panel door, Lockset Hardware, Painted Located in guestroom 454 bathroom. | 2027
82758 |  | (CN) CBV-122 Cabin 454,456,458 & Guest Lounge (CB-47 Cabin) | LMCO | Reposition dead front cover as per NEC Code Reference 408.38, 22" x 28" Metal Panel Box, Painted, Main Service Panel, 12 Breakers Trumbull Electric brands, 70-amp 3 wire, with main beaker. Located in utility closet | 2027
82758 |  | (CN) CBV-122 Cabin 454,456,458 & Guest Lounge (CB-47 Cabin) | LMCO | Repair or replace non illuminated exit sign as per IBC Reference Code 1013.3; 11" x 7" Wall Mounted, Emergency Exit Sign Located above egress walls in guest lounge | 2027
82758 |  | (CN) CBV-122 Cabin 454,456,458 & Guest Lounge (CB-47 Cabin) | RMDM | Refinish exterior log walls as they are past due; 8" diameter Stacked Log, Exterior Wall Frame Assembly, and Chinking mortar fill logs (297 LF), 2 x 6 framed in fill with 4" vertical siding at removed doors and windows. Located on all exterior walls including two exterior walls that are side-by-side between units 420 and 422 | 2027
82761 |  | (CN) CBV-123 Cabin 460&462, 464&466 (CB-49 Cabin & Rastrums) | LMCO | Replace outlet with GFCI outlet as per 210.8(B) Building other than dwelling units, Push Reset, GFCI Protected Receptacle Located in the women’s restroom | 2027
82762 |  | (CN) CBV-146 Cabin 459 & 461 (CB-50 Cabin) | LMCO | Provide proper clearance in front of electrical panel of at least 36 inches currently has 24" recommend relocation of panel as per code 408.20, 21" x 27" Metal Panel Box, Main Electrical Service Panel, General Electric brand, with, 12 Breakers, 100 Amp/3 Wire System Located in cabin 459 | 2027
82763 |  | (CN) CBV-147 Cabin 463 (CB-51 Cabin) | RMDM | Refinish exterior logs as they are past due; Stacked Log, Exterior Wall Frame Assembly, with Mortise and Tenon, and Chinking mortar fill 6" to 8" logs with 6" diameter corner posts and 6"x6" sill board. All exterior walls (107 LF) | 2027
82763 |  | (CN) CBV-147 Cabin 463 (CB-51 Cabin) | RMDM | Refinish exterior door as it is past time; 32" x 80" Wood, Solid Core, Exterior Entrance Door, Lockset with Key, Painted Five panel door. Located on the front of the cabin | 2027
82764 |  | (CN) CBV-148 Cabin 467 (CB-52 Cabin) | RMDM | Refinish exterior logs as they are past due; Stacked Log, Exterior Wall Frame Assembly, with Mortise and Tenon, and Chinking mortar fill 6" to 8" logs with 6" diameter corner posts and 6"x6" sill board. All exterior walls (107 LF) | 2027
82764 |  | (CN) CBV-148 Cabin 467 (CB-52 Cabin) | RMDM | Refinish exterior door as it is past time; 32" x 80" Wood, Solid Core, Exterior Entrance Door, Lockset with Key, Painted Five panel door. Located on the front of the cabin | 2027
82765 |  | (CN) CBV-149 Cabin 471 (CB-53 Cabin 471) | RMDM | Refinish exterior logs as they are past due; Stacked Log, Exterior Wall Frame Assembly, and Chinking mortar fill 8" logs - corner vertical posts (8 LF). (100 LF total) | 2027
82766 |  | (CN) CBV-124 Cabin 468 (CB-54 Cabin) | RMDM | Refinish exterior logs as they are past due; Stacked Log, Exterior Wall Frame Assembly, with Mortise and Tenon, and Chinking mortar fill 6" to 8" logs with 6" diameter corner posts and 6"x6" sill board. All exterior walls (107 LF) | 2027
82767 |  | (CN) CBV-125 Cabin 472 (CB-55 Cabin) | RMDM | Refinish exterior logs as they are past due; Stacked Log, Exterior Wall Frame Assembly, with Mortise and Tenon, and Chinking mortar fill 6" to 8" logs with 6" diameter corner posts and 6"x6" sill board. All exterior walls (107 LF) | 2027
82768 |  | (CN) CBV-126 Cabin 476 & 478 (CB-56 Cabin) | RMDM | Refinish exterior log walls as they are past due and need refinishing; 8" diameter Stacked Log, Exterior Wall Frame Assembly, with Mortise and Tenon, and Chinking mortar fill with 8" log posts at the outside corners (4 each 32 LF) and wood chinking on the interior, Stained. Located all exterior walls except around bathroom and between entry doors. (106 LF) | 2027
82769 |  | (CN) CBV-127 Cabin 480 (CB-57 Cabin) | RMDM | Refinish exterior logs as they are past time; Stacked Log, Exterior Wall Frame Assembly, with Mortise and Tenon, and Chinking mortar fill 6" to 8" logs with 6" diameter corner posts and 6"x6" sill board. All exterior walls (107 LF) | 2027
82770 |  | (CN) CBV-128 Cabin 484 (CB-58 Cabin) | RMDM | Refinish logs as they are past time; Stacked Log, Exterior Wall Frame Assembly, with Mortise and Tenon, and Chinking mortar fill 6" to 8" logs with 6" diameter corner posts and 6"x6" sill board. All exterior walls (107 LF) | 2027
82771 |  | (CN) CBV-129 Cabin 488 & 490 (CB-59 Cabin) | LMCO | Provide a minimum of 30" clearance space in front of electrical panel as per NEC Code Reference 110.26 21" x 27" Metal Panel Box, Main Electrical Service Panel, General Electric brand, with, 12 Breakers, 100 Amp/3 Wire System Located in cabin 490 | 2027
82771 |  | (CN) CBV-129 Cabin 488 & 490 (CB-59 Cabin) | RMDM | Refinish exterior log walls as they are past due and need refinishing; 8" diameter Stacked Log, Exterior Wall Frame Assembly, with Mortise and Tenon, and Chinking mortar fill with 8" log posts at the outside corners (4 each 32 LF) and wood chinking on the interior, Stained. Located all exterior walls except around bathroom and between entry doors. (106 LF) | 2027
82772 |  | (CN) CBV-130 Cabin 492 (CB-60 Cabin) | RMDM | Refinish exterior logs as they are past due; Stacked Log, Exterior Wall Frame Assembly, with Mortise and Tenon, and Chinking mortar fill 6" to 8" logs with 6" diameter corner posts and 6"x6" sill board. All exterior walls (107 LF) | 2027
82773 |  | (CN) CBV-158 Cabin 601 & 603 & 605 (CB-61 Cabin) | RMDM | Refinish exterior log walls as they are past due; 8" diameter Stacked Log, Exterior Wall Frame Assembly, with Mortise and Tenon, and Chinking mortar fill Stained. Located all exterior walls except around bathrooms and at entry doors. | 2027
82774 |  | (CN) CBV-150 Cabin 602 & 604 (CB-62 Cabin) | RMDM | Refinish exterior walls as their past due 8" diameter Stacked Log, Exterior Wall Frame Assembly, with Mortise and Tenon, and Chinking mortar fill Stained, and with 8" corner log posts (32 Total LF of log posts). Located all exterior walls except around bathroom (126 LF) | 2027
82775 |  | (CN) CBV-151 Cabin 606 & 608 (CB-63 Cabin) | DM | Refinish exterior log walls as they are past due; 8" diameter Stacked Log, Exterior Wall Frame Assembly, with Mortise and Tenon, and Chinking mortar fill Stained, and with 8" corner log posts (32 Total LF of log posts). Located all exterior walls except around bathroom (126 LF) | 2027
82776 |  | (CN) CBV-159 Cabin 609 & 611 & 613 (CB-64 Cabin) | LMCO | Provide required clear space in front of the electrical panel as per NEC Code Reference 110.26 (minimum of 30" 36"); 21" x 27" Metal Panel Box, Main Electrical Service Panel, General Electric brand, with, 16 Breakers, 100 Amp/3 Wire System Located in cabin 611 in the entry way. | 2027
82776 |  | (CN) CBV-159 Cabin 609 & 611 & 613 (CB-64 Cabin) | RMDM | Refinish log walls as they are past due and need refinishing; 8" diameter Stacked Log, Exterior Wall Frame Assembly, with Mortise and Tenon, and Chinking mortar fill Stained. Located all exterior walls except around bathrooms and at entry doors. | 2027
82777 |  | (CN) CBV-152 Cabin 610 (CB-65 Cabin 610) | DM | Caulk major cracks in the Exterior log walls on all sides of the building (approximately 175 LF) Stacked Log, Exterior Wall Frame Assembly, with Mortise and Tenon, and Chinking mortar fill 8" to 10" logs. Located at all exterior walls. | 2027
82777 |  | (CN) CBV-152 Cabin 610 (CB-65 Cabin 610) | RMDM | Refinish exterior siding as it is past due, 1"x6". Exterior Siding Material, Planks. (65"x84"). Located on the south and west sides of the building. | 2027
82778 |  | (CN) CBV-153 Cabin 612 & 614 (CB-66 Cabin) | LMCO | Provide required clear space in front of the electrical panel (Minimum of 30") currently it has only 24" as per the NEC Code Reference 110.26; 21" x 27" Metal Panel Box, Main Electrical Service Panel, General Electric brand, with, 12 Breakers, 100 Amp/3 Wire System Located in cabin 612 | 2027
82778 |  | (CN) CBV-153 Cabin 612 & 614 (CB-66 Cabin) | RMDM | Refinish exterior log walls as they are past due and need refinishing; 8" diameter Stacked Log, Exterior Wall Frame Assembly, with Mortise and Tenon, and Chinking mortar fill with 8" log posts at the outside corners (4 each 32 LF) and wood chinking on the interior, Stained. Located all exterior walls except around bathroom and between entry doors. (106 LF) | 2027
82779 |  | (CN) CBV-160 Cabin 617 (CB-68 Cabin) | RMDM | Refinish exterior logs as they are past due; Stacked Log, Exterior Wall Frame Assembly, with Mortise and Tenon, and Chinking mortar fill with 6" to 8" logs. Located around the entire building (101 LF) | 2027
82781 |  | (CN) CBV-155 Cabin 624 & 626 & 628 (CB-70 Cabin) | DM | Replace rotting trim at doorways to prevent water infiltration and further damage. 1" x 2" Wood, Exterior Wall Trim, Painted Located at openings and in-fill framing. | 2027
82781 |  | (CN) CBV-155 Cabin 624 & 626 & 628 (CB-70 Cabin) | LMCO | Install proper breaker ties at the electrical panel located in room 624 as per 2010 NEC Code Reference 240.15 (B)(1), 20" x 26" Metal Panel Box, Main Electrical Service Panel, 16 Breakers, 100 Amp/3 Wire System Trumbull electric. Located in room 624 | 2027
82782 |  | (CN) CBV-162 Cabin 625 & 627 (CB-71 Cabin) | RMDM | Refinish exterior log walls as they are past due; 8" diameter Stacked Log, Exterior Wall Frame Assembly, with Mortise and Tenon, and Chinking mortar fill and wood chinking on the interior, Stained. Located all exterior walls except around bathroom and between entry doors. (123 LF) | 2027
82783 |  | (CN) CBV-163 Cabin 629 (CB-72 Cabin) | DM | Replace missing gravel on roof; Tar & Gravel, Roof Finish, with 4" metal drip edge Located over the entire structure | 2027
82783 |  | (CN) CBV-163 Cabin 629 (CB-72 Cabin) | RMDM | Refinish exterior log walls as they are past due and in need of refinishing; Stacked Log, Exterior Wall Frame Assembly, with Mortise and Tenon, and Chinking mortar fill with 6" to 8" logs. Located around the entire building (101 LF) | 2027
82784 |  | (CN) CBV-156 Cabin 630 & 632 (CB-73 Cabin) | LMCO | Provide required clear space in front of electrical panel as per NEC Code Reference 110.26 (minimum of 30" x 36"); 21" x 27" Metal Panel Box, Main Electrical Service Panel, General Electric brand, with, 12 Breakers, 100 Amp/3 Wire System Located in the entry of cabin 630. | 2027
82784 |  | (CN) CBV-156 Cabin 630 & 632 (CB-73 Cabin) | RMDM | Refinish exterior log walls as they are past due and need to be refinished; 8" diameter Stacked Log, Exterior Wall Frame Assembly, with Mortise and Tenon, and Chinking mortar fill with 8" log posts at the outside corners (4 each 32 LF) and wood chinking on the interior, Stained. Located all exterior walls except around bathroom and between entry doors. (106 LF) | 2027
82785 |  | (CN) CBV-157 Cabin 634 & 638 (CB-74 Cabin) | DM | Replace rotting trim around doors to prevent further decay and water infiltration. 2" x 6" Wood, Painted Located at either side of both entry doors. (26.67 LF) | 2027
82785 |  | (CN) CBV-157 Cabin 634 & 638 (CB-74 Cabin) | RMDM | Refinish exterior logs to prevent further decay and weathering. Stacked Log, Exterior Wall Frame Assembly, with Notched Corners, overhanging, and Chinking mortar fill 6 inch to 8-inch logs with chinking located on exterior and interior of walls. Four exterior walls per building (170 LF). | 2027
82785 |  | (CN) CBV-157 Cabin 634 & 638 (CB-74 Cabin) | RMDM | Refinish exterior siding to prevent further weathering and potential rot. 1" x 6" Wood, Exterior Siding Material, Painted Wood plank siding oriented vertically. Located on all 2x6 exterior wall framing at entries and on south of cabin 634. | 2027
82786 |  | (CN) CBV-164 Cabin 637 (CB-75 Cabin 637) | RMDM | Refinish exterior logs as they are past due Stacked Log, Exterior Wall Frame Assembly, with Mortise and Tenon, and Chinking mortar fill 6" to 8" logs with wood chinking on the inside. Located all exterior walls. (49 LF) | 2027
82786 |  | (CN) CBV-164 Cabin 637 (CB-75 Cabin 637) | RMDM | Refinish exterior log walls as they are past time; Stacked Log, Exterior Wall Frame Assembly, with Mortise and Tenon, and Chinking mortar fill 6" to 8" logs with wood chinking on the inside. Located all exterior walls. (49 LF) | 2027
82787 |  | (CN) CBV-165 Cabin 639 (CB-76 Cabin 639) | CRDM | Replace as it is past it's useful life; 1" x 6" Wood, Fascia Board, Painted. Located on the west and east perimeter of the roof eaves. (60 LF) | 2027
82787 |  | (CN) CBV-165 Cabin 639 (CB-76 Cabin 639) | RMDM | Refinish exterior logs as they are past due Stacked Log, Exterior Wall Frame Assembly, with Mortise and Tenon, and Chinking mortar fill 6" to 8" logs with wood chinking on the inside. Located all exterior walls. (49 LF) | 2027
82791 |  | (CN) CBV-173 Cabin 801 & 803 (CB-78 Cabin) | DM | Replace waistband piping at roof penetrations as they have been broken (2 at 2 LF); Galvanized, Waste & Vent Piping, with 4-inch piping | 2027
82791 |  | (CN) CBV-173 Cabin 801 & 803 (CB-78 Cabin) | RMDM | Refinish exterior log walls as they are past due. Stacked Log, Exterior Wall Frame Assembly, with Notched Corners, overhanging, and Chinking mortar fill 6-to-8-inch logs with chinking mortar fill on the exterior and wood chinking on the interior. (133 LF) | 2027
82792 |  | (CN) CBV-167 Cabin 802 & 804 (CB-79 Cabin) | LMCO | Replace GFCI as per 210.8(B) Building other than dwelling units, Push Reset, GFCI Protected Receptacle Located next to sink in the bathroom of 804 | 2027
82794 |  | (CN) CBV-168 Cabin 806 (CB-81 Cabin) | RMDM | Refinish exterior logs as they are past due; Stacked Log, Exterior Wall Frame Assembly, with Mortise and Tenon, and Chinking mortar fill 6" to 8" logs with 6" diameter corner posts and 6"x6" sill board. All exterior walls (107 LF) | 2027
82796 |  | (CN) CBV-169 Cabin 810 (CB-83 Cabin) | RMDM | Refinish exterior log walls as they are past due; Stacked Log, Exterior Wall Frame Assembly, with Mortise and Tenon, and Chinking mortar fill with 6" to 8" logs. Located around the entire building (101 LF) | 2027
82797 |  | (CN) CBV-170 Cabin 830 & 832 (CB-84 Cabin) | RMDM | Refinish exterior log walls as they are past due; 8" diameter Stacked Log, Exterior Wall Frame Assembly, with Mortise and Tenon, and Chinking mortar fill and chinking on the interior, Stained. Located all exterior walls except around bathrooms. (107 LF) | 2027
82798 |  | (CN) CBV-176 Cabin 831 & 833 (CB-85 Cabin) | LMCO | Install missing junction box cover as per 2010 NEC Code Reference 250.35.3, 12 Gauge Wire, Electrical Wiring Distribution Lines, with junction boxes Located throughout the building to electrical fixtures (780 LF) | 2027
82798 |  | (CN) CBV-176 Cabin 831 & 833 (CB-85 Cabin) | LMLS | Replace missing knockout cover in electrical panel; 16" x 26" Metal Panel Box, Main Electrical Service Panel, Square D brand, with, 20 Breakers, 100 Amp/3 Wire System Located in the utility room on exterior of building | 2027
82799 |  | (CN) CBV-171 Cabin 834 & 836 (CB-86 Cabin) | RMDM | Refinish exterior log walls as they as past time when they should have been refinished; 8" diameter Stacked Log, Exterior Wall Frame Assembly, with Mortise and Tenon, and Chinking mortar fill and chinking on the interior, Stained. Located all exterior walls except around bathrooms. (107 LF) | 2027
82800 |  | (CN) CBV-177 Cabin 835 & 837 (CB-87 Cabin) | RMDM | Refinish exterior log walls as they are past due; 8" diameter Stacked Log, Exterior Wall Frame Assembly, with Mortise and Tenon, and Chinking mortar fill and wood chinking on the interior, Stained. Located all exterior walls except around bathroom and between entry doors. (123 LF) | 2027
82801 |  | (CN) CBV-172 Cabin 838 & 840 (CB-88 Cabin) | RMDM | Refinish exterior log walls as they are past due; 8" diameter Stacked Log, Exterior Wall Frame Assembly, with Mortise and Tenon, and Chinking mortar fill and chinking on the interior, Stained. Located all exterior walls except around bathrooms. (107 LF) | 2027
82803 |  | (CN) CBV-178 Cabin 839 (CB-89 Cabin 839) | RMDM | Refinish exterior logs as they are past due; Stacked Log, and Chinking mortar fill, Exterior Wall Frame Assembly, 6" to 8" logs with chinking on both exterior and interior. Located on the west, north and east sides of structure. (94 LF) | 2027
82804 |  | (CN) CBV-179 Cabin 1001 & 1003 (CB-90 Cabin) | RMDM | Refinish exterior logs as they are past due. Stacked Log, Exterior Wall Frame Assembly, and Chinking mortar fill 6" to 8" logs with chinking on both exterior and interior. (100 LF) | 2027
82807 |  | (CN) CBV-181 Cabin 1005 & 1007 (CB-92 Cabin) | DM | Refinish exterior logs as they are past due; 8" diameter Stacked Log, Exterior Wall Frame Assembly, with Mortise and Tenon, and Chinking mortar fill and wood chinking on the interior, Stained. Located all exterior walls. (106 LF) | 2027
82811 |  | (CN) CBV-154 Cabin 616 & 620 & 622 (CB-67 Cabin) | LMCO | Provide required clear space in front of the electrical panel per NEC Code Reference 110.26 (Minimum of 30" X 36”) (Currently there is only 24"); 21" x 27" Metal Panel Box, Main Electrical Service Panel, General Electric brand, with, 16 Breakers, 100 Amp/3 Wire System Located in cabin 622 in the entry way. | 2027
82811 |  | (CN) CBV-154 Cabin 616 & 620 & 622 (CB-67 Cabin) | RMDM | Refinish exterior log walls as they are past due and in need of refinishing; 8" diameter Stacked Log, Exterior Wall Frame Assembly, with Mortise and Tenon, and Chinking mortar fill Stained. Located all exterior walls except around bathrooms and at entry doors. | 2027
82813 |  | (CN) CBV-186 Cabin 1014 (CB-96 Cabin) | DM | Refinish exterior logs as that your past time;.8" diameter Squared off Log, Exterior Wall Frame Assembly, with Mortise and Tenon, and Chinking mortar fill Logs with wood chinking on the inside. Located around the exterior of the building. (110 LF) | 2027
82824 |  | (CN) CBV-201 B Linen Building #2 (CB-107 Linen Bldg. #2) | RMDM | Refinish exterior log walls as they are past due; 5" diameter Stacked Log, Exterior Wall Frame Assembly, with Mortise and Tenon stacked logs. Interior walls have 1 inch wood fill in between stacked logs. Located around the entire building | 2027
82827 |  | (CN) CBV-207 H Linen Building #8 (CB-110 Linen Bldg. #8) | RMDM | Refinish exterior log walls as they are past due. 5" diameter Stacked Log, Exterior Wall Frame Assembly, with Mortise and Tenon stacked logs. Interior walls have 1 inch wood fill in between stacked logs. Located around the entire building | 2027
82829 |  | (CN) CBV-209 J Linen Building #10 (CB-112 Linen Bl | LMCO | Install weatherproof covering for exterior GFCI outlet as per the NEC 210.8 iii; Push Reset, GFCI Protected Receptacle Located on the south exterior wall of the building | 2027
82830 |  | (CN) CBV-203 D Linen Building #4 (CB-113 Linen Bldg. #4) | RMDM | Refinish exterior log walls as they are past due; 5" diameter Stacked Log, Exterior Wall Frame Assembly, with Mortise and Tenon stacked logs. Interior walls have 1 inch wood fill in between stacked logs. Located around the entire building | 2027
82833 |  | (CN) CBV-901 Tent Village Office/Restrooms (CB-116) | LMAC | Add protective covering for the hot water and drainpipes under the accessible lavatory/sinks in the men's and women's restrooms as per ADAABAG Section 606.5; 20" x 17" Porcelain, Lavatory, mounted on top of Countertop (5) each Located in both men's and women's restrooms | 2027
82833 |  | (CN) CBV-901 Tent Village Office/Restrooms (CB-116) | LMCO | Add Seismic strapping shall be 2” wide around the top 1/3 and the bottom 1/3 as per UPC (Uniformed Plumbing Code) Reference 507.2; Electric, Water Heater - Residential Rehem, 50 Gallon No. 1 - serial no. RH 0507R11600, Model no. 82V52-2. No. 2 - serial no. R 0584109842, Model no. 62V-52D; located in the office. | 2027
82834 |  | (CN) CBV-905 Tent Village Upper Rest Rooms (CB-117) | DM | Repair missing gravel on the ridge and along edge of roof, and repair holes in the roof at the ridge; Tar & Gravel, Roof Finish, with 2" metal drip edge Located over the entire roof (This component is part of the historic fabric and or character feature of the building.) | 2027
82834 |  | (CN) CBV-905 Tent Village Upper Rest Rooms (CB-117) | LMAC | Change door hardware on both Men's and Women's entry doors to allowable hardware as per ADAABAG Section 309.4. And adjust self-closing devise to remain open for a minimum of 5 seconds as per ADAABAG Section 404.2.8.1. 32" x 80" Wood, Solid Core, with Self-Closing Device, Deadbolt and Door Handle, Painted, Exterior Entrance Door, And 8"x32" kick plate. Located to men’s and women’s restroom. | 2027
82834 |  | (CN) CBV-905 Tent Village Upper Rest Rooms (CB-117) | LMAC | Add protective covering for the hot water and drainpipes under the accessible lavatory/sinks in the men's and women's restrooms as per ADAABAG Section 606.5. 19" x 16" Porcelain, mounted on top of Countertop, Lavatory, Located in men’s (4) and women’s (5) restroom. | 2027
82834 |  | (CN) CBV-905 Tent Village Upper Rest Rooms (CB-117) | LMAC | Replace faucet at the accessible sinks with easy to operate with one hand and do not require tight grasping, pinching, or twisting of the wrist as per ADAABAG Section 606.4,309. 6" x 5" Chrome Finish, Faucet - Single Valve, Located on sinks in the men’s and women’s restroom. | 2027
82834 |  | (CN) CBV-905 Tent Village Upper Rest Rooms (CB-117) | LMCO | Add Seismic strapping shall be 2” wide around the top 1/3 and the bottom 1/3 as per UPC (Uniformed Plumbing Code) Reference 507.2; Electric, Water Heater - Residential, Rheem, 50 Gallon Model #62v-52D Serial #0785109111. Located in the utility room | 2027
82834 |  | (CN) CBV-905 Tent Village Upper Rest Rooms (CB-117) | LMCO | Replace the missing knockout on the electrical panel located in the utility room as per NEC Reference Code 408.7 & 110.12 (A) | 2027
82835 |  | (CN) CBV-801 RV Park Office (CB-118 Visitor RV Park Office) | LMAC | Add Kick plates to provide the necessary 10" smooth surface extending the full width of the bottom of the push side of the door as per ADAABAG Section 404.2.10; 36" x 80" Exterior Entrance Door, 5 panel door. Located on the east side of building. | 2027
82835 |  | (CN) CBV-801 RV Park Office (CB-118 Visitor RV Park Office) | LMAC | Replace door lockset with on that does not require tight grasping, tight pinching or twisting of the wrist to operate as per ADAABAG Section 309.4; 36" x 80" Exterior Entrance Door, 5 panel door. Located on the east side of building. | 2027
82835 |  | (CN) CBV-801 RV Park Office (CB-118 Visitor RV Park Office) | LMAC | Replace door lockset with on that does not require tight grasping, tight pinching or twisting of the wrist to operate as per ADAABAG Section 309.4; 28" x 76" Standard Interior Door, 5 panel door. Located door from back office to the break room and to the restroom. | 2027
82835 |  | (CN) CBV-801 RV Park Office (CB-118 Visitor RV Park Office) | LMAC | Add Kick plates to provide the necessary 10" smooth surface extending the full width of the bottom of the push side of the door as per ADAABAG Section 404.2.10; 28" x 76" Standard Interior Door, 5 panel door. Located door from back office to the break room and to the restroom | 2027
82835 |  | (CN) CBV-801 RV Park Office (CB-118 Visitor RV Park Office) | LMAC | Replace door lockset with on that does not require tight grasping, tight pinching or twisting of the wrist to operate as per ADAABAG Section 309.4; 32" x 80" Standard Interior Door, 5 panel door. Located between the front office and the back office | 2027
82835 |  | (CN) CBV-801 RV Park Office (CB-118 Visitor RV Park Office) | LMAC | Add Kick plates to provide the necessary 10" smooth surface extending the full width of the bottom of the push side of the door as per ADAABAG Section 404.2; 32" x 80" Standard Interior Door, 5 panel door. Located between the front office and the back office | 2027
82836 |  | (CN) CBV-802 RV Park Comfort Station Loop A (CB-119 | CRDM | Replace as it is past its useful life: Electric, Rheem, 50 Gallon, Water Heater - Residential, Model number 82V52-2. Serial # RH 0511R10016 Located in the utility chase. | 2027
82836 |  | (CN) CBV-802 RV Park Comfort Station Loop A (CB-119 | DM | Repair leaking water faucet. 6" x 8" Chrome Finish, Faucet - Dual Handle, Located on the double sink in the service sink room. | 2027
82836 |  | (CN) CBV-802 RV Park Comfort Station Loop A (CB-119 | LMAC | Replace thresholds with one that has a maximum of 1/2" from the floor as per ADAABAG Section 404.2.5; 36" x 84" Exterior Entrance Door, Built-up door with 2"x6" planks with 1/2" covering with a 10"x34" plate on the front and backside of the door and a 24“ x 24“ view window with obscured glass. Located at entrance to the men’s and women’s restrooms. | 2027
82836 |  | (CN) CBV-802 RV Park Comfort Station Loop A (CB-119 | LMAC | Replace door locksets with ones that have a shape that is easy to grasp with one hand and not require tight grasping, pinching, or twisting of the wrist to operate, per ADAABAG Section 309.4; 36" x 84" Exterior Entrance Door, Built-up door with 2"x6" planks with 1/2" covering with a 10"x34" plate on the front and backside of the door and a 24“ x 24“ view window with obscured glass. Located at entrance to the men’s and women’s restrooms. | 2027
82836 |  | (CN) CBV-802 RV Park Comfort Station Loop A (CB-119 | LMAC | Adjust self-closer so that from an opening position of 90 degrees , the door will take at least 5 seconds to move to a point 12 degrees from the latch, measured to the leading edge of the door; Per ADAABAG Section 404.2.8.1; 36" x 84" Exterior Entrance Door, Built-up door with 2"x6" planks with 1/2" covering With a 10"x34" plate on the front and backside of the door and a 24“ x 24“ view window with obscured glass. Located at entrance to the men’s restroom. | 2027
82836 |  | (CN) CBV-802 RV Park Comfort Station Loop A (CB-119 | LMAC | Add self-closing hinge on accessible stall doors as per ADAABAG Section 604.8.1.2.; 70" x 84" x 58" Fabricated Toilet Partition, With 2 - 24" doors. Located in the men’s restroom | 2027
82836 |  | (CN) CBV-802 RV Park Comfort Station Loop A (CB-119 | LMAC | Add self-closing hinge on accessible stall doors as per ADAABAG Section 604.8.1.2.; 105" x 84" x 58" Fabricated Toilet Partition, with 3 - 24"x58" doors, located in the women's restroom. | 2027
82836 |  | (CN) CBV-802 RV Park Comfort Station Loop A (CB-119 | LMAC | Add protecting covering for the hot water and drainpipes under the accessible lavatory/sink in the men's rest room as per ADAABAG Section 606.5; 19" x 17" Lavatory, Located in the men’s restroom. | 2027
82836 |  | (CN) CBV-802 RV Park Comfort Station Loop A (CB-119 | LMAC | Relocate flush control handle so that it is located on the open side of the water closet as per ADAABAG Section 604.6; Porcelain, with Tank, Floor Mounted, with Manual Handle Flush Valve, Water Closet, Located in the men's restroom | 2027
82836 |  | (CN) CBV-802 RV Park Comfort Station Loop A (CB-119 | LMCO | Remove obstructions in front of the electrical panel as per the NEC Code reference 110.26; 16" x 24" Metal Panel Box, General Electric brand, with, 24 Breakers, 100 Amp/3 Wire System, Main Electrical Service Panel, Located in the utility chase. | 2027
82837 |  | (CN) CBV-803 RV Park Comfort Station Loop F (CB-120 | LMLS | Secure Electrical Box cover so the reset can be used without taking off cover. 6" x 12" x 629" Metal Panel Box, General Electric brand, with, 100 Amp/3 Wire System, Service Disconnect, Single Breaker Located on the north wall of the utility chase next to the panel. | 2027
82838 |  | (CN) CBV-804 RV Park Comfort Station Loop L (CB-12 | CRDM | Replace at end of useful life: Electric, Rheem, 50 Gallon, Water Heater - Residential, Model number 82V52-2. Serial # RH 0511R10016 Located in the utility chase. | 2027
82838 |  | (CN) CBV-804 RV Park Comfort Station Loop L (CB-12 | DM | Repair broken windowpane in the men's restroom on the south side of the building next to the service sink room. 40" x 32" Steel, Single Pane, with aluminum screen, Glazed Window, Hopper style window with obscured glass two panes. | 2027
82839 |  | (CN) CBV-005 Service Station (RV) (CB-122)) | DM | Add missing siding at rooftop junction gable end. (36 SF); Batt and Board, Exterior Siding Material, Batt & Board, Painted One by seven batts spaced 13 inches apart | 2027
82839 |  | (CN) CBV-005 Service Station (RV) (CB-122)) | RMDM | Paint fascia board as it is past due, to extend its useful life. 4" X 12", Wood, Fascia Board, Unfinished, (This component is part of the historic fabric of the building), Located on the west and east edges of the roof (non-gable roof edges). (170 LF) | 2027
82841 |  | (CN) CBV-003 Convenience Store (CB-123 Service Station) | DM | Replace approximately 10% of missing gravel on the roof. Tar & Gravel, with 2" metal drip edge, Roof Finish located over entire roof structure. | 2027
82841 |  | (CN) CBV-003 Convenience Store (CB-123 Service Station) | LMAC | Adjust Door closer to sweep period of the closer adjusted so that from an open position of 90 degrees, the door will take at least 5 seconds to move to a point 12 degrees from the latch. As per ADAABAG Section 404.2.8.1. 60" x 80" Aluminum, with Self-Closing Device, Deadbolt and Door Handle, Factory Finish, Glazed Store Front Door, Double door, With a 60"x28" transom window above. Located at front of store. | 2027
82841 |  | (CN) CBV-003 Convenience Store (CB-123 Service Station) | LMAC | Adjust Door closer to sweep period of the closer adjusted so that from an open position of 90 degrees, the door will take at least 5 seconds to move to a point 12 degrees from the latch. As per ADAABAG Section 404.2.8.1. 36" x 80" Metal, with Self-Closing Device, Deadbolt and Door Handle, Painted, Exterior Entrance Door, With a 10" x 34" kick plate. Located on the west exterior of the building. | 2027
82841 |  | (CN) CBV-003 Convenience Store (CB-123 Service Station) | LMAC | Add self-closing hinge on accessible stall doors as per ADAABAG Section 604.8.1.2. 60 " x 88 " x 58 " Metal, Fabricated Toilet Partition, Stainless steel with 1- 36"x58" door. Located in the men’s and women’s restroom. | 2027
82841 |  | (CN) CBV-003 Convenience Store (CB-123 Service Station) | LMAC | Add pull handles on the interior of the accessible stall doors as per ADAABAG Section 604.8.1.2; 404.2.7; 60 " x 88 " x 58 " Metal, Fabricated Toilet Partition, Stainless steel with 1- 36"x58" door. Located in the men’s and women’s restroom. | 2027
82841 |  | (CN) CBV-003 Convenience Store (CB-123 Service Station) | LMAC | Adjust coat hooks so they are positioned at a maximum of 48" as per ADAABAG Section .308.3; 603.4; 60 " x 88 " x 58 " Metal, Fabricated Toilet Partition, Stainless steel with 1- 36"x58" door. Located in the men’s and women’s restroom. | 2027
82841 |  | (CN) CBV-003 Convenience Store (CB-123 Service Station) | LMAC | Relocate water closets located in the accessible stalls so the center line of the water closet is between 16"-18" from the closest wall, as per ADAABAG Section 604.2. Porcelain, with Tank, Floor Mounted, with Manual Handle Flush Valve, Water Closet, Located (1) in the men’s and (1) in the women’s restroom. | 2027
82841 |  | (CN) CBV-003 Convenience Store (CB-123 Service Station) | LMAC | Change flush control on the Accessible water closet in the women's restroom to be on the open side of the water closet as per; ADAABAG Section 604.6; Porcelain, with Tank, Floor Mounted, with Manual Handle Flush Valve, Water Closet, Located (1) in the men’s and (1) in the women’s restroom. | 2027
82842 |  | (CN) CBV-305 Employee West Dorm (CB-124 Employee Housing) | DM | Replace Missing VCT Tile, Dorm room 24 and room 34; 12" x 12" VCT Vinyl, Interior Floor Covering Material, | 2027
82844 |  | (CN) CBV-303 Employee South Dorm (CB-125 Employee Housing) | DM | Replace Broken Tiles, Broken floor tiles at cased opening. 9" x 9" Vinyl, Interior Floor Covering Material, | 2027
82844 |  | (CN) CBV-303 Employee South Dorm (CB-125 Employee Housing) | LMFS | Fill around wall penetrations in firewall located in the laundry room. Gypsum Board, Interior Wall Covering Material, | 2027
82846 |  | (CN) CBV-304 Employee East Dorm (CB-126 Employee H | DM | Repair Water Damage, located in utility closet above doorway, Drywall, Painted Located in men’s and women’s bathrooms, utility closet, 260LF | 2027
82846 |  | (CN) CBV-304 Employee East Dorm (CB-126 Employee H | DM | Replace Floor Tiles, located in dorm 3, 24, 34, and upstairs hallway; 9" x 9" Vinyl, Interior Floor Covering Material, | 2027
82846 |  | (CN) CBV-304 Employee East Dorm (CB-126 Employee H | DM | Replace Warped Ceiling Tiles, 2' x 2' Suspended Acoustic, Interior Ceiling Covering Material, Factory Finished Located in men’s and women’s bathrooms, utility closet, | 2027
82846 |  | (CN) CBV-304 Employee East Dorm (CB-126 Employee H | DM | Replace missing Glass on Fire Hose Cabinets, located in second floor hallway, Metal, Fire Hose Cabinet With valve located mid hallway on each hallway | 2027
82846 |  | (CN) CBV-304 Employee East Dorm (CB-126 Employee H | LMFS | Add Gypsum to Access Door for Fire Code, 2' x 2' Wood, Attic Access with 1x2 trim, located in hallway | 2027
82846 |  | (CN) CBV-304 Employee East Dorm (CB-126 Employee H | LMFS | Repair Phone Cabinet to be Fire Rated, located in hallway, Plywood, Interior Wall Covering Material, painted (Shadow board) Located on all walls in all dorm rooms and hallways. | 2027
82848 |  | (CN) CBV-302 Employee North Dorm (CB-127 Employee Housing) | DM | Add missing soffit vents on north eave of structure to improve ventilation. | 2027
82848 |  | (CN) CBV-302 Employee North Dorm (CB-127 Employee Housing) | DM | Replace Missing 12" x 12" VCT Vinyl, Interior Floor Covering Material, Factory Finish Located in hallways of the building and common area and all dorm rooms | 2027
82848 |  | (CN) CBV-302 Employee North Dorm (CB-127 Employee Housing) | DM | Repair Water Damage, Water damage at wall near bathroom; Drywall, Interior Ceiling Covering Material, Painted. | 2027
82848 |  | (CN) CBV-302 Employee North Dorm (CB-127 Employee Housing) | LMFS | Remove FRP attached to wall covering gypsum between bathroom and dorm 8. Drywall, Interior Wall Covering Material, Painted | 2027
82850 |  | (CN) CBV-301 EmpVlgOffice/Laundry/RecHall/Maint (CB-128) | DM | Repair Sliding Pocket Door, sliding pocket door gets stuck when closing, Dorm 5, | 2027
82850 |  | (CN) CBV-301 EmpVlgOffice/Laundry/RecHall/Maint (CB-128) | DM | Repair Sliding Pocket Door, has no handle, Dorm room 7 | 2027
82850 |  | (CN) CBV-301 EmpVlgOffice/Laundry/RecHall/Maint (CB-128) | LMCO | Install panic hardware on Rec room doors require panic hardware based on occupancy in an assembly occupancy. 72" x 80" Wood, Divided Lite, Exterior Entrance Door, with Self-Closing Device, Round Handle, painted 22" x 36" lights, Metal clad. | 2027
82850 |  | (CN) CBV-301 EmpVlgOffice/Laundry/RecHall/Maint (CB-128) | LMLS | Test for possible asbestos with green wrap on copper piping. Copper, 2 1/2 Diameter, Hot & Cold Water, Supply Piping, located in boiler room from main boiler with valve shut off. | 2027
82854 |  | (CN) CBV-006 Warehouse (CB-130 Warehouse) | CRDM | Replace damaged roll up door 16'' X 12', Aluminum, Overhead Door, Overhead Door with Tracks, Located at south end of building | 2027
82854 |  | (CN) CBV-006 Warehouse (CB-130 Warehouse) | CRDM | Replace as it is beyond its useful life; Service Equipment Plug, 240 Volt Outlet, Located on the east exterior wall in the northeast corner. | 2027
82854 |  | (CN) CBV-006 Warehouse (CB-130 Warehouse) | DM | Repair broken safety glass window at bottom lite of door. 44" x 84" Steel, Lockset with Key, Painted, Exterior Entrance Door With 32 x 38 dual lite safety glass window. With padlock hasp. Located at north end of south structure. | 2027
82854 |  | (CN) CBV-006 Warehouse (CB-130 Warehouse) | DM | Replace damage siding in multiple locations along structure where forklift has gouged and scored Galvanized Corrugated Siding, Exterior Siding Material, Painted, 1 1/2-inch corrugations, Located at exterior of entire structure | 2027
82854 |  | (CN) CBV-006 Warehouse (CB-130 Warehouse) | DM | Replace damaged siding in multiple locations along the structure where forklift has gouged and scored Galvanized Corrugated Siding, Exterior Siding Material 1 1/2-inch depth corrugation. Located at south building. North, East, and West walls at the north end of the south building (3 walls). 1,395 S.F. | 2027
82855 |  | (CN) CBV-017 Corrals Office (CB-131 Corral Office) | CRDM | Replace as they are past their useful life; Ungrounded, 2-Wire Receptacle Located throughout the building | 2027
82855 |  | (CN) CBV-017 Corrals Office (CB-131 Corral Office) | LMAC | Replace door hardware so it will not require tight grasping, tight pinching or twisting of the wrist to operate as per ADAABAG Section 309.4, on the 34" x 80" Wood, Solid Core, Lockset with Key, Painted, Exterior Entrance Door, with three 23“x 9“glass panels that are single pane. Located on the north entry door to the office. | 2027
82855 |  | (CN) CBV-017 Corrals Office (CB-131 Corral Office) | LMAC | Replace door hardware so it will not require tight grasping, tight pinching or twisting of the wrist to operate as per ADAABAG Section 309.4 on the 30" x 78" Hollow Core - Wood, Lockset Hardware, Factory Finish, Standard Interior Door, dividing the two interior rooms. | 2027
82855 |  | (CN) CBV-017 Corrals Office (CB-131 Corral Office) | RMDM | Repaint deck as it is past due; 2" x 6" Wood, Exterior deck, Painted Deck protrudes from north wall 52 inches and protrudes from the east wall 76 inches. Deck was constructed on 2x10's 24" O.C. Located on the north and east walls | 2027
82857 |  | (CN) CBV-018 Corrals Bunk House & Tack Room (CB-13 | CRDM | Replace as it is beyond its useful life; 26" x 80" Wood, Deadbolt, Painted, Exterior Entrance Door, Water heater access door. Located on the south wall in the southwest corner | 2027
82857 |  | (CN) CBV-018 Corrals Bunk House & Tack Room (CB-13 | CRDM | Replace at end of useful life: 138" x 72" Wood, Painted, Exterior deck, 1 x 8 tongue, and groove panels. With 4x4 frame 58" O.C. 4x4 post = 3 @ 15 linear feet. Patio has 2x4 rim board that is 12 lf. Located at tack room entry | 2027
82857 |  | (CN) CBV-018 Corrals Bunk House & Tack Room (CB-13 | LMCO | Add Seismic strapping shall be 2” wide around the top 1/3 and the bottom 1/3 as per UPC (Uniformed Plumbing Code) Reference 507.2; Water heater in the mechanical closet along the south exterior. | 2027
82859 |  | (CN) CBV-020 Corrals Hay Barn (CB-133 Hay Shed) | DM | Replace missing structural member at left side of front of structure. 12" diameter Wood, Structural Support Post 12 feet tall each, spaced 12 feet apart at walls on sides of structure and 15 apart at front and rear structure. With 6-inch diameter diagonal supports 4 feet long | 2027
82859 |  | (CN) CBV-020 Corrals Hay Barn (CB-133 Hay Shed) | DM | Repair roof beam connection at center of structure on right side as it is improperly secured. 6" diameter Wood, Structural Support Beam 48 feet long each. | 2027
82859 |  | (CN) CBV-020 Corrals Hay Barn (CB-133 Hay Shed) | DM | Repair damage rafter at 12th row from front on left side, and second from front. 2" x 6" Rafters - Wood, Pitched Roof Construction, @ 24 O.C., with tongue & groove roof decking | 2027
82863 |  | (CN) CBV-111 Manager's Cabin (CB-136 Manager Unit) | CRDM | Replace as it is past its useful life; 6" diameter Battery Operated, Smoke Detector, Located in the kitchen and each of the two bedrooms and in living room | 2027
82863 |  | (CN) CBV-111 Manager's Cabin (CB-136 Manager Unit) | LMCO | Encase electrical wire in kitchen in conduit. 12 Gauge Wire, Electrical Wiring Distribution Lines. Per NEC Article 334.15. | 2027
82863 |  | (CN) CBV-111 Manager's Cabin (CB-136 Manager Unit) | LMLS | Test 9 x 9“ VCT tile for asbestos. 9" x 9" VCT, Interior Floor Covering Material Located at entry and closet on the south side of the building. | 2027
82864 |  | (CN) CBV-(CB-137 Employee RV Park Restroom/Laundry) | DM | Replace missing baseboard on the north wall and east wall of the laundry. Rubber, Baseboard Trim 4" tall | 2027
82864 |  | (CN) CBV-(CB-137 Employee RV Park Restroom/Laundry) | DM | Repair damage drywall in the laundry room (12 SF) | 2027
82864 |  | (CN) CBV-(CB-137 Employee RV Park Restroom/Laundry) | LMCO | Add Seismic strapping shall be 2” wide around the top 1/3 and the bottom 1/3 as per UPC (Uniformed Plumbing Code) Reference 507.2, Electric, Water Heater - Residential, A.O. Smith, 120 Gallon Located in the laundry room | 2027
82864 |  | (CN) CBV-(CB-137 Employee RV Park Restroom/Laundry) | LMCO | Add Seismic strapping shall be 2” wide around the top 1/3 and the bottom 1/3 as per UPC (Uniformed Plumbing Code) Reference 507.2; Electric, Water Heater - Residential, Rheem, 120 Gallon Model #81V-120D Serial #0383114531. Located in the laundry room | 2027
83356 |  | (CN) JNY-001 Main Lodge Building (JE-01 Main Lodge) | DM | Extend waste pipe Plastic - ABS, Waste & Vent Piping, with 2-inch piping, 2 Diameter Located on roof. | 2027
83356 |  | (CN) JNY-001 Main Lodge Building (JE-01 Main Lodge) | LMAC | Replace hardware so that the door is easily operated with closed fist as per ADAABAG Section 309.4 on the 36" x 80" metal, self-closer, round standard handle, painted, standard Interior Door, door stopper, located at staff kitchen bathroom. | 2027
83356 |  | (CN) JNY-001 Main Lodge Building (JE-01 Main Lodge) | LMAC | Insulate water and drainpipes under accessible lavatory/sink so they are covered or configured to protect against contact as per ADAABAG Section 606.5 on the 22" x 18" Porcelain, Wall Hung, Wall Mounted, Lavatory, Located in staff employee restroom. | 2027
83356 |  | (CN) JNY-001 Main Lodge Building (JE-01 Main Lodge) | LMAC | Adjust rim to urinal so that it does not exceed 17" above the floor as per ADAABAG Section 605.2 on the 12" x 21" x 15" Porcelain, Tankless, Wall Mounted, with Manual Handle Flush Valve, Urinal, Located in staff employee restroom. | 2027
83356 |  | (CN) JNY-001 Main Lodge Building (JE-01 Main Lodge) | LMAC | Adjust flush control so it is on the open side of the water closet as per ADAABAG Section 604.6 on the 20" x 28" x 31" Porcelain, with Tank, Floor Mounted, with Manual Handle Flush Valve, Water Closet, Located in staff employee restroom. | 2027
83356 |  | (CN) JNY-001 Main Lodge Building (JE-01 Main Lodge) | LMAC | Adjust flush control so it is located on the open side of the water closet as per ADAABAG Section 604.6 on the porcelain tank, Floor Mounted, with Push Button Flush Valve, Water Closet, women’s restroom off main lobby. | 2027
83356 |  | (CN) JNY-001 Main Lodge Building (JE-01 Main Lodge) | LMFS | Add spark arrester 48" x 36" x 36" Fireplace 26’ chimney flue with terra cotta lining. Located in sitting area | 2027
83356 |  | (CN) JNY-001 Main Lodge Building (JE-01 Main Lodge) | RMDM | Repoint approximately 10% of chimney, 4' x 7' x 23' tall, tapered Stone Chimney, Clad in natural River rock with mortar. (This component is part of the historic fabric and or character feature of the building.) | 2027
83357 |  | (CN) JNY-300 General Manager Cabin (JE-02 Manager Resid) | LMCO | Add Seismic strapping shall be 2” wide around the top 1/3 and the bottom 1/3 as per UPC (Uniformed Plumbing Code) Reference 507.2; 20" diameter Electric, Rheem, 50 Gallon, Water Heater - Residential, Located in closet off living room. Serial No. 0185101846; Model No. 62V-52D. | 2027
83357 |  | (CN) JNY-300 General Manager Cabin (JE-02 Manager Resid) | RMDM | Restain exterior logs as they are past due. 8" diameter Stacked Log, with Notched Corners, overhanging, and Chinking mortar fill, Exterior Wall Frame Assembly, Located around exterior of building (116 LF). | 2027
83358 |  | (CN) JNY-100 Glacier Lily (JE-03 Glacier Lily) | CRDM | Replace as it is past it's useful life; Galvanized, knob-turn, Hose bib, located on the main water line coming into the building on the east exterior wall | 2027
83358 |  | (CN) JNY-100 Glacier Lily (JE-03 Glacier Lily) | RMDM | Restain fascia board as it is past due; fascia board 120 L.F.) Fascia board located around the perimeter of the roof. | 2027
83359 |  | (CN) JNY-101 Fireweed (JE-04 Fireweed) | RMDM | Refinish fascia board as it is past due, 1" x 6" Wood, Fascia Board, (105 LF) Stained wood. Located at low ends of roof and low ends of covered patio. | 2027
83367 |  | (CN) JNY-103 Violet (JE-06 Violet) | DM | Secure loose Water Closet, Porcelain, with Tank, Floor Mounted, with Manual Handle Flush Valve Located in the bathroom | 2027
83369 |  | (CN) JNY-105 Balsam Root/Delphinium (JE-08) | RMDM | Refinish exterior screen doors they are past due; 36" x 80" Wood, Screen Door, and with Handle, Painted Two panel at bottom and screen on top. Located at the entrances of each cabin | 2027
83370 |  | (CN) JNY-106 Blue Flax/Elderberry (JE-09 Blue Flax/Elderb) | LMAC | Provide a 10" smooth surface extending the full width of the door as per ADAABAG Section 404.2.10; 36" x 80" Wood, Screen Door, and with Handle, Painted Two panel at bottom and screen on top. Located at the entrances of Elderberry cabin | 2027
83370 |  | (CN) JNY-106 Blue Flax/Elderberry (JE-09 Blue Flax/Elderb) | LMAC | Change door locks with one that does not require tight grasping, tight pinching, or twisting of the wrist to operate; as per ADAABAG Section 309.4; 36" x 80" Wood, Screen Door, and with Handle, Painted Two panel at bottom and screen on top. Located at the entrances of the Elderberry cabin | 2027
83370 |  | (CN) JNY-106 Blue Flax/Elderberry (JE-09 Blue Flax/Elderb) | LMAC | Adjust threshold so that it is beveled and that the floor level changes a maximum of 1/2" at accessible doors and the bevel with a slope is no greater than 1:2 as per ADAABAG Section 309.4; 36" x 80" Wood, Exterior Entrance Door, Deadbolt and Door Handle, Stained 6 panel door. Located at entrance to the Elderberry cabin | 2027
83370 |  | (CN) JNY-106 Blue Flax/Elderberry (JE-09 Blue Flax/Elderb) | LMAC | Change door locks with one that does not require tight grasping, tight pinching, or twisting of the wrist to operate; as per ADAABAG Section 309.4; 36" x 80" Wood, Exterior Entrance Door, Deadbolt and Door Handle, Stained 6 panel door. Located at entrance to the Elderberry cabin | 2027
83370 |  | (CN) JNY-106 Blue Flax/Elderberry (JE-09 Blue Flax/Elderb) | LMAC | Add grab bar at the foot of the tub that is at least 24" long, per ADAABAG Section 607.1.1.2; in the bathroom of Elderberry. | 2027
83370 |  | (CN) JNY-106 Blue Flax/Elderberry (JE-09 Blue Flax/Elderb) | LMAC | Replace Tub diverter so the controls are easily and operable and useable with one hand, without tight grasping, pinching, or twisting of the wrist to operate, per ADAABAG Section 309.4; 6" diameter Metal, Mixing Valve - Tub/Shower Located in Elderberry bathroom above bathtub. | 2027
83370 |  | (CN) JNY-106 Blue Flax/Elderberry (JE-09 Blue Flax/Elderb) | LMAC | Adjust the thermostat height to be a maximum of 48" and unobstructed as per ADAABAG Section 308.2.1, 308.2.2; 3" x 4" Manual controlled, Thermostat Located in the Elderberry cabin. | 2027
83371 |  | (CN) JNY-107 Yarrow/Tansy (JE-10 Yarrow/Tansy) | LMAC | Change door locks with one that does not require tight grasping, tight pinching, or twisting of the wrist to operate; as per ADAABAG Section 309.4; 36" x 80" Wood, Screen Door, and with Handle, Painted Two panel at bottom and screen on top. Located at the entrances of Tansy | 2027
83371 |  | (CN) JNY-107 Yarrow/Tansy (JE-10 Yarrow/Tansy) | LMAC | Provide a 10" smooth surface extending the full width of the door as per ADAABAG Section 404.2.10; 36" x 80" Wood, Screen Door, and with Handle, Painted Two panel at bottom and screen on top. Located at the entrances of Tansy. | 2027
83371 |  | (CN) JNY-107 Yarrow/Tansy (JE-10 Yarrow/Tansy) | LMAC | Adjust threshold so that are beveled and that the floor level changes a maximum of 1/2" at accessible doors and the bevel with a slope is no greater than 1:2 as per ADAABAG Section 309.4; 36" x 80" Wood, Exterior Entrance Door, Deadbolt and Door Handle, Stained 6 panel door. Located at entrance to Tansy | 2027
83371 |  | (CN) JNY-107 Yarrow/Tansy (JE-10 Yarrow/Tansy) | LMAC | Change door locks with one that does not require tight grasping, tight pinching, or twisting of the wrist to operate; as per ADAABAG Section 309.4; 36" x 80" Wood, Exterior Entrance Door, Deadbolt and Door Handle, Stained 6 panel door. Located at entrance to Tansy | 2027
83371 |  | (CN) JNY-107 Yarrow/Tansy (JE-10 Yarrow/Tansy) | LMAC | Add grab bar at the foot of the tub that is at least 24" long, per ADAABAG Section 607.1.1.2; located in the shower in Tansy. | 2027
83371 |  | (CN) JNY-107 Yarrow/Tansy (JE-10 Yarrow/Tansy) | LMAC | Add a horizontal grab bar at the head of the tub that is at least 12" long as per ADAABAG Section 607.4.2.3; located in the Tansy bathroom. | 2027
83371 |  | (CN) JNY-107 Yarrow/Tansy (JE-10 Yarrow/Tansy) | LMAC | Replace Tub diverter so the controls are easily and operable and useable with one hand, without tight grasping, pinching, or twisting of the wrist to operate, per ADAABAG Section 309.4; 6" diameter Metal, Mixing Valve - Tub/Shower Located in bathrooms above bathtub in Tansy. | 2027
83371 |  | (CN) JNY-107 Yarrow/Tansy (JE-10 Yarrow/Tansy) | LMAC | Adjust the thermostat height to be a maximum of 48" and unobstructed as per ADAABAG Section 308.2.1, 308.2.2; 3" x 4" Manual controlled, Thermostat Located in Tansy | 2027
83372 |  | (CN) JNY-108 Water Lily (JE-11 Water Lily) | DM | Secure log railing around the perimeter of the deck; 20' x 7' Wood, Stained, Exterior deck, Deck material is made up of 2 x 6 wood planks with 2 x 10 wood floor joists located 36 inches on center. Includes two risers at 6 inches with a tread depth of 12 inches. Stairs are constructed of 2 x 6 wood members with a 1x12 when board that wraps the entire perimeter of deck. There is an 8-inch diameter log on the south end that the wood joists tie into to support the deck. There are (6) 6-inch vertical log supports that are 58 inches tall that support the 4-inch diameter log railing. Log railing has two sets of rails one 18 inches off the deck and the other is 38 inches off the deck. Located on the West side of the building. (140 SF) | 2027
83377 |  | (CN) JNY-112 Primrose/Phlox (JE-15 Primrose/Phlox) | DM | Refinish exterior log siding as it is past due;6" diameter Wood, Exterior Siding Material, Painted 1/4 log siding with chinking. Located around the bathroom at the rear of the building. | 2027
83379 |  | (CN) JNY-113 Lupine (JE-16 Lupine) | RMDM | Refinish fascia board as it is past due; 1" x 6" Wood, Fascia Board, Stained wood. Located at low ends of roof and low ends of covered patio. (116 LF) | 2027
83383 |  | (CN) JNY-115 Indian Paintbrush (JE-18 Indian Paintbrush) | LMCO | Provide proper clearance space in front of electrical panel (30 x 36-inch clearance min) as per NEC Code Reference 110.26. | 2027
83385 |  | (CN) JNY-117 Harebell (JE-20 Harebell) | LMCO | Provide the proper (30 x 36-inch clearance min) as per NEC Code Reference 110.26. 11" x 17" Metal Panel Box, Main Electrical Service Panel, Square D brand, with, 12 Breakers, 100 Amp/3 Wire System Located in the water heater closet. | 2027
83386 |  | (CN) JNY-118 Hollyhock (JE-21 Hollyhock) | DM | Secured toilet to floor it is loose needs to be secured. Porcelain, Water Closet, with Tank, Floor Mounted, with Manual Handle Flush Valve Located in the bathroom | 2027
83390 |  | (CN) JNY-121 Gentian (JE-24 Gentian) | CRDM | Replace as it is past it's useful life; Galvanized, knob-turn, Hose bib, located on the main water line coming into the building on the east exterior wall | 2027
83390 |  | (CN) JNY-121 Gentian (JE-24 Gentian) | DM | Repair large crack in patio the runs the width of the patio; 13' x 8' Concrete, Entrance Stoop - Pad (104 S.F.) 4" Deep, Located at entry door | 2027
83390 |  | (CN) JNY-121 Gentian (JE-24 Gentian) | RMDM | Refinish fascia board as it is past due; (120 L.F.) Fascia board will need to be replaced or re-stained as it is past due | 2027
83391 |  | (CN) JNY-122 Coneflower (JE-25 Coneflower) | CRDM | Replace as it is past it's useful life; galvanized, knob-turn, Hose bib, located on the main water line coming into the building on the east exterior wall | 2027
83391 |  | (CN) JNY-122 Coneflower (JE-25 Coneflower) | RMDM | Refinish fascia board as it is past due; (120 L.F.) Fascia board will need to be replaced or re-stained as it is past due | 2027
83407 |  | (CN) JNY-124 Chokecherry (JE-27 Chokecherry) | DM | Replace the end of the ridge beam rafter tail as it has rotted out; Rafters - Log Timber, Pitched Roof Construction @ 24 O.C. (587 S.F.) with 8" log rafters | 2027
83409 |  | (CN) JNY-126 Bluebell (JE-29 Bluebell) | LMCO | Install new latching mechanism to ensure that electrical panel shuts. 12" x 18" Metal Panel Box, Main Electrical Service Panel, Square D brand, with, 12 Breakers, 100 Amp/3 Wire System Located in the utility closet | 2027
83415 |  | (CN) JNY-003 Corrals Tack Room/Bunk House (JE-32 Stables) | DM | Remove dirt from crawlspace vent on southeast corner of building | 2027
83415 |  | (CN) JNY-003 Corrals Tack Room/Bunk House (JE-32 Stables) | DM | Replace window to right of front porch as it is missing its outer pane. 44" x 46" Wood, Glazed Window, Sliding, Double Pane, Painted, with aluminum screen | 2027
83415 |  | (CN) JNY-003 Corrals Tack Room/Bunk House (JE-32 Stables) | LMCO | Add Seismic strapping shall be 2” wide around the top 1/3 and the bottom 1/3 as per UPC (Uniformed Plumbing Code) Reference 507.2; Electric, A.O. Smith, 40 Gallon, Water Heater - Commercial, Located in the loft. | 2027
83415 |  | (CN) JNY-003 Corrals Tack Room/Bunk House (JE-32 Stables) | RMDM | Restain Wood Decking as is beyond the time to Restain. 2" x 6" Composite Planking, Stained, Deck Flooring Material, Located at rear porch (160 SF). | 2027
83415 |  | (CN) JNY-003 Corrals Tack Room/Bunk House (JE-32 Stables) | RMDM | Restain Wood Decking because it is beyond it's time to be stained. 2" x 6" Wood Planking for, Stained, Located at front porch (25 SF). | 2027
83417 |  | (CN) JNY-302 Rock Chuck/Mdl/Jedediah (JE-35 Rock Chuck/Jed) | LMCO | Add electrical conduit to wire that runs to the ceiling fan in the middle unit. 12 Gauge Wire, with junction boxes, Electrical Wiring Distribution Lines, (35 LF) As per the NEC Article 34.15. | 2027
83417 |  | (CN) JNY-302 Rock Chuck/Mdl/Jedediah (JE-35 Rock Chuck/Jed) | RMDM | Refinish all exterior log walls as they are past due; Stacked Log, with Mortise and Tenon, and Chinking mortar fill, All exterior walls (1,392 LF). | 2027
83418 |  | (CN) JNY-303 Moran (JE-36 Moran) | RMDM | Restain the exterior of the log wall as it is past time. Stacked Log, with Mortise and Tenon, and Chinking mortar fill, Exterior Wall Frame Assembly, All exterior walls. (764 LF). | 2027
83420 |  | (CN) JNY-305 Symmetry/St. John/TT (JE-38 Symmetry/St. John) | LMCO | Add electrical conduit to electrical wire that runs by the door in the St. John unit (10 LF) As per the NEC Article 34.15. 12 Gauge Wire. | 2027
83420 |  | (CN) JNY-305 Symmetry/St. John/TT (JE-38 Symmetry/St. John) | RMDM | Refinish exterior logs as they are past due; 8" diameter Stacked Log, with Mortise and Tenon, and Chinking mortar fill, Exterior Wall Frame Assembly, Exterior log walls. (1,224 LF). | 2027
83420 |  | (CN) JNY-305 Symmetry/St. John/TT (JE-38 Symmetry/St. John) | RMDM | Refinished window trim as it is past due; located on the south, east, and west sides of the building, repaint to match existing. (42 LF) | 2027
83421 |  | (CN) JNY-306 South (JE-39 South) | DM | Repair the drain valve that leaks on the water heater to the exterior wall on the south side in the east bedroom. Electric, Water Heater - Residential, Bradford White, 50 Gallon Model number. M250t6ds-1ncww | 2027
83421 |  | (CN) JNY-306 South (JE-39 South) | LMCO | Add electrical Conduit from the wall to the electrical wall heater where it stops short of the heater and the where is exposed and is taped off. (2-1/2' of additional conduit) NEC article 334.15. 16" x 18" Metal, Electric Wall Heater, Berko. Located in the bathroom. | 2027
83421 |  | (CN) JNY-306 South (JE-39 South) | LMCO | Label Electrical panel located on south exterior wall inside the cabinet as per NEC Article 110.22. 18" x 14" Metal Panel Box, Square D brand, with, 20 Breakers, 100 Amp/3 Wire System, Main Service Panel, Located on the east exterior wall inside the built-in electrical cabinet. | 2027
83421 |  | (CN) JNY-306 South (JE-39 South) | LMCO | Provide Clear space of at least 30" in front of electrical panel, currently the electrical enclosure prohibits the panel door from opening completely. NEC Article 110.26. 18" x 14" Metal Panel Box, Square D brand, with, 20 Breakers, 100 Amp/3 Wire System, Located on the east exterior wall inside the built-in electrical enclosure. | 2027
83421 |  | (CN) JNY-306 South (JE-39 South) | LMCO | Add electrical conduit to exposed wire in bathroom. NEC Article 334.15. 12 Gauge Wire, with junction boxes, Electrical Wiring Distribution Lines. (15 LF) | 2027
83421 |  | (CN) JNY-306 South (JE-39 South) | LMLS | Provide a cover plate on the junction box in the west bedroom that has exposed wires, per NEC Code reference 408.38 | 2027
83426 |  | (CN) JNY-310 Storm (JE-44 Storm) | LMCO | Provide clear space in front of panel of the lease 30 inches as per NEC code Reference 110.26. 13" x 16" Metal Panel Box, Square D brand, with, 16 Breakers, 100 Amp/3 Wire System, Electrical Sub Panel, Located on the east interior wall. | 2027
83426 |  | (CN) JNY-310 Storm (JE-44 Storm) | RMDM | Refinish exterior walls has they are past due, Stacked Log, with Mortise and Tenon, and Chinking mortar fill, Exterior Wall Frame Assembly, 6" & 8" logs. Located exterior walls of the building (873 LF of logs). | 2027
83428 |  | (CN) JNY-312 Buck/Static (JE-46 Buck/Static) | RMDM | Refinish exterior logs as they are past due; Stacked Log, with Notched Corners, overhanging, and Chinking mortar fill, Exterior Wall Frame Assembly, 8"-10" diameter. Located at exterior walls (1,080 LF of Logs). | 2027
83428 |  | (CN) JNY-312 Buck/Static (JE-46 Buck/Static) | RMDM | Refinish trim as it is way past due; 1" x 4" Wood, Painted, Exterior Wall Trim, Located around doors and windows. (102 LF). | 2027
83428 |  | (CN) JNY-312 Buck/Static (JE-46 Buck/Static) | RMDM | Repaint windows as they are past due; 69" x 40" Wood, Sliding, Single Pane, Painted, with wood screen, Glazed Window, Located north and south walls. | 2027
83429 |  | (CN) JNY-313 Prospector/Grand (JE-47) | RMDM | Repaint roof support posts as they are past due; Wood, Structural Support Post, 6-inch diameter, painted. Located at both porches to support roof. (72 Total LF). | 2027
83429 |  | (CN) JNY-313 Prospector/Grand (JE-47) | RMDM | Repaint electrical panel enclosure as it is past due; 17" x 26" x 60" box for electrical panel and junction box. Constructed of plywood and 2" x 4" framing with one by four trim and asphalt shingle roofing. Has 14“x 38“latching access door. Located on the west side of the building. | 2027
83430 |  | (CN) JNY-301 Employee Bath House/Laundry (JE-48 Bath) | DM | Repair hole in Gypsum Board, Interior Wall Covering Material, painted located in the laundry room. | 2027
83430 |  | (CN) JNY-301 Employee Bath House/Laundry (JE-48 Bath) | LMCO | Add Seismic strapping shall be 2” wide around the top 1/3 and the bottom 1/3 as per UPC (Uniformed Plumbing Code) Reference 507.2; 26" diameter Electric, Rheem, 120 Gallon, Water Heater - Residential, Located in the Landry room. (Right) Model No. - 81V-12OD, Serial No. - 0488112847, (Left) Model No. 82V120-2, serial No. 1007E00156. | 2027
83432 |  | (CN) B - JNS-001 Jenny Lake Store | LMAC | Add protecting covering for the hot water and drainpipes under the lavatory in the rest room as per ADAABAG Section 606.5; 17" x 19" Porcelain, Wall Hung, Wall Mounted, Lavatory, Located in the employee restroom. | 2027
83432 |  | (CN) B - JNS-001 Jenny Lake Store | LMAC | Move water closet so that the center of the water closet is between 16"-18" from the closest wall as per ADAABAG Section 604.2; Porcelain, with Tank, Floor Mounted, with Manual Handle Flush Valve, Water Closet, Located in the employee restroom. | 2027
83432 |  | (CN) B - JNS-001 Jenny Lake Store | LMAC | Relocate flush control handle so that it is located on the open side of the water closet as per ADAABAG Section 604.6; Porcelain, with Tank, Floor Mounted, with Manual Handle Flush Valve, Water Closet, Located in the employee restroom. | 2027
83458 |  | (CN) JLL-001 Main Lodge Building (JL-1 Main Lodge) | CRDM | Replace at end of useful life: 22" x 48" Aluminum - Louvered Vent, Utility Opening - Exterior Wall, With screen. Located on north wall of freight elevator shaft | 2027
83458 |  | (CN) JLL-001 Main Lodge Building (JL-1 Main Lodge) | CRDM | Replace at end of useful life: 34" x 48" Aluminum - Louvered Vent, Utility Opening - Exterior Wall, (11.3 SF Each) With mesh screen (2 ea.). Located on the north and south walls of the freight elevator shaft and the vent shaft of 48") | 2027
83458 |  | (CN) JLL-001 Main Lodge Building (JL-1 Main Lodge) | CRDM | Replace as it is beyond its useful life; 160" x 38" Wood, Interior Window, 2 abandoned windows on East wall of retail storage garage. (~13.333 lf) | 2027
83458 |  | (CN) JLL-001 Main Lodge Building (JL-1 Main Lodge) | CRDM | Replace as the door is part its useful life; 30" x 80" Solid Core - Wood, Standard Interior Door, Lockset Hardware, Painted With wood grill Measuring 21 inches by 21 inches. Located in the hallway into China room. Located in the hallway into Potato closet. | 2027
83458 |  | (CN) JLL-001 Main Lodge Building (JL-1 Main Lodge) | CRDM | Replace at the end of useful life: 36" x 80" Solid Core - Wood, Lockset Hardware, Painted, Standard Interior Door, with acoustical tiles measuring 72“ x 29“ on the interior side of the door, Located between third floor storage 1 and 2. | 2027
83458 |  | (CN) JLL-001 Main Lodge Building (JL-1 Main Lodge) | CRDM | Replace as it is beyond useful life nonfunctioning wall heater in restrooms 16" x 20" x 4" Metal, Electric Wall Heater With integral radial thermostat, Located in West wall of kitchen men’s and women’s restrooms. | 2027
83458 |  | (CN) JLL-001 Main Lodge Building (JL-1 Main Lodge) | CRDM | Replace at end of useful life: Push Reset, GFCI Protected Receptacle, With the weatherproof cover. Located on the duct work at the captiveaire exhaust air fans on the roof | 2027
83458 |  | (CN) JLL-001 Main Lodge Building (JL-1 Main Lodge) | CRDM | Replace exhaust fans as they are past their useful life, 10" x 10" Through the Ceiling, Whole Room Exhaust Fan Ceiling mounted, Brand: Broan, includes 4-inch flexible duct to exterior (12LF), Located in Kitchen restrooms both men's and women's. | 2027
83458 |  | (CN) JLL-001 Main Lodge Building (JL-1 Main Lodge) | CRDM | Replace gas fired space heater past useful life, 36" x 30" x 24" Ceiling Mounted, Gas Fired Space Heater, Dayton with 8-inch exhaust flue through ceiling (65 LF), Model number 681757, 140,000 BTU output, Located centered over boiler room. | 2027
83458 |  | (CN) JLL-001 Main Lodge Building (JL-1 Main Lodge) | DM | Reaffix insulation to underside of floor deck above boiler room. 4" x 14" Concrete, Floor Frame Assembly, @ 36" O.C. Precast concrete I beam with 4 x 14 concrete bridging at mid span. Metal decking with 6-inch concrete floor above joists. 2 inches fiberglass insulation | 2027
83458 |  | (CN) JLL-001 Main Lodge Building (JL-1 Main Lodge) | DM | Repaint exterior louver due to weather damage. (4) located in the west north and east walls of the north generator room. | 2027
83458 |  | (CN) JLL-001 Main Lodge Building (JL-1 Main Lodge) | DM | Repair stonework at the front building entry appears to have settled and is pulling away from the lintel; Natural Stone, Exterior Wall, with mortar Veneer located at the Porte cochere | 2027
83458 |  | (CN) JLL-001 Main Lodge Building (JL-1 Main Lodge) | DM | Replace windowpane with BB holes.211" x 84" Aluminum, Glazed Window, Awning, Tempered Safety Glass, with aluminum screen Double pane, window divided into 16 sections. 8 sections are awning with aluminum screens. Located on the north side of the reservation offices room. | 2027
83458 |  | (CN) JLL-001 Main Lodge Building (JL-1 Main Lodge) | DM | Paint Window Frames and Seals; 104" x 38" Wood, Glazed Window, Stationary, Single Pane, Painted Window is divided into two sections (52x38 each). Located on the north side of the trumpeter room. | 2027
83458 |  | (CN) JLL-001 Main Lodge Building (JL-1 Main Lodge) | DM | Replace Damaged block. 6" Fixed Partition, Ceramic tile block. Located throughout kitchen area (~455.77 lf) | 2027
83458 |  | (CN) JLL-001 Main Lodge Building (JL-1 Main Lodge) | DM | Repair damage from water leak in the ceiling of the kitchen on the south end of the building; Drop Ceiling Assembly Metal channel suspended ceiling structure. | 2027
83458 |  | (CN) JLL-001 Main Lodge Building (JL-1 Main Lodge) | DM | Adjust door as the Carpet impedes proper closure of guestroom doors 18; 36" x 80" Solid Core - Wood, Standard Interior Door, Self-Closer, Lockset Hardware, Painted. | 2027
83458 |  | (CN) JLL-001 Main Lodge Building (JL-1 Main Lodge) | DM | Replace vinyl in Mural room men’s and women’s bathroom. Vinyl, Interior Floor Covering Material, Factory Finish Sheet vinyl. | 2027
83458 |  | (CN) JLL-001 Main Lodge Building (JL-1 Main Lodge) | DM | Investigate possible water damage in NW corner of West Conference hallway; 24" x 48" Suspended Acoustic, Interior Ceiling Covering Material, Painted | 2027
83458 |  | (CN) JLL-001 Main Lodge Building (JL-1 Main Lodge) | DM | Replace missing/broken ceiling tiles in pioneer grill kitchen; 24" x 48" Suspended Acoustic, Interior Ceiling Covering Material Food grade finish. | 2027
83458 |  | (CN) JLL-001 Main Lodge Building (JL-1 Main Lodge) | DM | Investigate possible water damage in antelope 1; 24" x 48" Suspended Acoustic, Interior Ceiling Covering Material, Painted Waffle pattern. | 2027
83458 |  | (CN) JLL-001 Main Lodge Building (JL-1 Main Lodge) | DM | Fix or replace damaged tile in vault office; 24" x 24" Suspended Acoustic, Interior Ceiling Covering Material, Painted Waffle | 2027
83458 |  | (CN) JLL-001 Main Lodge Building (JL-1 Main Lodge) | DM | Investigate and fix water damage in kitchen, Drywall, Interior Ceiling Covering Material, Painted. | 2027
83458 |  | (CN) JLL-001 Main Lodge Building (JL-1 Main Lodge) | DM | Test ceiling tile and mastic for possible asbestos in blower room. 12" x 12" Mineral Fiber Panel, Interior Ceiling Covering Material, Factory Finished. | 2027
83458 |  | (CN) JLL-001 Main Lodge Building (JL-1 Main Lodge) | DM | Replace missing tiles in blower room on the roof; 12" x 12" Mineral Fiber Panel, Interior Ceiling Covering Material, Factory Finished | 2027
83458 |  | (CN) JLL-001 Main Lodge Building (JL-1 Main Lodge) | DM | Repair leaking shut off valve half-inch galvanized located near the attic access on the eastern side of the kitchen by the sheriff’s office window in the attic above is leaking causing a large amount of water damage to the ceiling. | 2027
83458 |  | (CN) JLL-001 Main Lodge Building (JL-1 Main Lodge) | DM | Repair Steam pipe is not draining properly causing damage to cabinets and structures near the drain. Hot and cold supply lines running East and West in the laundry room, also 20 linear feet from soft water system to drain. | 2027
83458 |  | (CN) JLL-001 Main Lodge Building (JL-1 Main Lodge) | DM | Repair leak that is causing grease to leak over the roof. 40" x 30" Kitchen Exhaust Hood/Fan with a 18"x 18" x 120" ducting, Located on roof above kitchen. | 2027
83458 |  | (CN) JLL-001 Main Lodge Building (JL-1 Main Lodge) | DM | Add structure above roof finish as walking surface at stair landing. Current landing consists only of roof surface which is insufficient. Metal, Exterior Stair Construction Assembly, Straight-Run Design, with Steel Pipe Railing, with closed riser in two runs. 40" wide, 20 treads @ 11", 21 risers @ 7", 44"x 46" landing, with 2" metal railing @ 116LF, 44" wide stairs, 23 treads @ 14", 24 risers @ 7 inches. Located near loading dock on south side of building. | 2027
83458 |  | (CN) JLL-001 Main Lodge Building (JL-1 Main Lodge) | LMAC | Provide a 10” smooth surface extending the full width of the bottom of the push side of the door as per code ADAABAG Section 404.2.10, 72" x 119" Aluminum, Store Front, Exterior Entrance Door, with Self-Closing Device, Deadbolt and Door Handle, Factory Finish Double hung door, push bar, with 35" transom window above. Located on the east side of the Lower Lobby. | 2027
83458 |  | (CN) JLL-001 Main Lodge Building (JL-1 Main Lodge) | LMAC | Adjust threshold to have a maximum change of 1/2" at accessible doors and beveled with a slope no greater than 1:2; as per ADAABAG Section 404.2.5; 72" x 84" Aluminum, Store Front, Glazed Store Front Door, with Push Bar, Painted Double hung doors (72" x 84"), with transom (72" x 41") above, sidelight (72" x 96") to the left of the door. Window (72" x 74") and transom (72" x 24") above doors and sidelights. Second pairing is a mirror of the first. Located on the southwest corner of the Blue Heron room. | 2027
83458 |  | (CN) JLL-001 Main Lodge Building (JL-1 Main Lodge) | LMAC | Replace handle hardware so that the handles, pulls, latches, locks, or other operating devices on doors have a shape that is easy to grasp with one hand and not require tight grasping, tight pinching or twisting of the wrist to operate as per code ADAABAG Section 309.4,36" x 80" Solid Core - Wood, Standard Interior Door, Lockset Hardware, Painted Located in the hall to Human resources office 5. Top half has single pane light measuring 20 inches wide by 24 inches tall. | 2027
83458 |  | (CN) JLL-001 Main Lodge Building (JL-1 Main Lodge) | LMAC | Replace handle hardware so that the handles, pulls, latches, locks, or other operating devices on doors have a shape that is easy to grasp with one hand and not require tight grasping, tight pinching or twisting of the wrist to operate as per code ADAABAG Section 309.4,28" x 80" Hollow Core - Wood, Glazed Interior Door, Lockset Hardware, Painted With single pane measuring 24 inches wide and 34 inches tall. Located at Finance Office 3 Director, And Finance Office 4 Asst DOF | 2027
83458 |  | (CN) JLL-001 Main Lodge Building (JL-1 Main Lodge) | LMAC | Replace handle hardware so that the handles, pulls, latches, locks, or other operating devices on doors have a shape that is easy to grasp with one hand and not require tight grasping, tight pinching or twisting of the wrist to operate as per code ADAABAG Section 309.4, 36" x 80" Hollow Core - Wood, Standard Interior Door, Lockset Hardware, Factory Finish Located in HR offices 1, 2 and 4 | 2027
83458 |  | (CN) JLL-001 Main Lodge Building (JL-1 Main Lodge) | LMAC | Replace handle hardware so that the handles, pulls, latches, locks, or other operating devices on doors have a shape that is easy to grasp with one hand and not require tight grasping, tight pinching or twisting of the wrist to operate as per code ADAABAG Section 309.4, 36" x 80" Solid Core - Wood, Standard Interior Door, Lockset Hardware, Factory Finish Located in executive hallway into food and beverage office 1. Located in South conference hallway into convention banquets office. Located in South conference hallway into food and beverage office 3 | 2027
83458 |  | (CN) JLL-001 Main Lodge Building (JL-1 Main Lodge) | LMAC | Replace handle hardware so that the handles, pulls, latches, locks, or other operating devices on doors have a shape that is easy to grasp with one hand and not require tight grasping, tight pinching or twisting of the wrist to operate as per code ADAABAG Section 309.4, 36" x 78" Solid Core - Wood, Standard Interior Door, Lockset Hardware, Factory Finish Located in executive hallway into food and beverage office 2. | 2027
83458 |  | (CN) JLL-001 Main Lodge Building (JL-1 Main Lodge) | LMAC | Replace handle hardware so that the handles, pulls, latches, locks or other operating devices on doors have a shape that is easy to grasp with one hand and not require tight grasping, tight pinching or twisting of the wrist to operate as per code ADAABAG Section 309.4, 36" x 80" Solid Core - Wood, Standard Interior Door, Self-Closer, Lockset Hardware, Painted (1) Located in the southeast corner of the executive office 4 main area. (1) Located on the north wall of the business office. | 2027
83458 |  | (CN) JLL-001 Main Lodge Building (JL-1 Main Lodge) | LMAC | Replace handle hardware so that the handles, pulls, latches, locks, or other operating devices on doors have a shape that is easy to grasp with one hand and not require tight grasping, tight pinching or twisting of the wrist to operate as per code ADAABAG Section 309.4, 36" x 80" Solid Core - Wood, Glazed Interior Door, Lockset Hardware, Painted Full lite door, Located in executive office six hotel operations. | 2027
83458 |  | (CN) JLL-001 Main Lodge Building (JL-1 Main Lodge) | LMAC | Replace doorknob with one that do not require tight grasping, pinching, or twisting of the wrist as per ADAABAG Section 309.4 on doors 1) Located in executive office five Vice President. (1) Located in executive office three director of sales and marketing. (1) Located in executive office, (1) nationals’ sales manager. (1) Door to the guest business center, executive offices.32" x 80" Solid Core - Wood, Standard Interior Door, Lockset Hardware, Painted. | 2027
83458 |  | (CN) JLL-001 Main Lodge Building (JL-1 Main Lodge) | LMAC | Adjust threshold so that the floor level changes a maximum of 1/2" at accessible doors and beveled with a slope no greater than 1/2 as per code ADAABAG Section 404.2.5, 32" x 80" Solid Core - Wood, Standard Interior Door, Lockset Hardware, Painted located from the executive offices to the VP office. | 2027
83458 |  | (CN) JLL-001 Main Lodge Building (JL-1 Main Lodge) | LMAC | Replace doorknobs with one that do not require tight grasping, pinching, or twisting of the wrist; as per ADAABAG Section 309.4; Located in executive office 2 Conference planning manager. Door28" x 80" Solid Core - Wood, Standard Interior Door, Lockset Hardware, Painted Upper single pane obscure glazing measuring 20 inches wide and 36 inches tall. | 2027
83458 |  | (CN) JLL-001 Main Lodge Building (JL-1 Main Lodge) | LMAC | Replace door handle located on the south wall of the business center Door to the guest business center, executive offices, and other employee offices throughout the main floor, along with employee’s access doors throughout the building have knob style hardware that requires tight grasping and twisting of rest to operate. Need replacing according to ADAABAG Section 309.4. | 2027
83458 |  | (CN) JLL-001 Main Lodge Building (JL-1 Main Lodge) | LMAC | Replace doorknobs with one that don't require tight grasping, pinching, or twisting of rest to operate. According to ADAABAG Section 309.4; .26" x 78" Solid Core - Wood, Standard Interior Door, Lockset Hardware, Painted With single pane glazing measuring 18 inches wide by 34 tall. Located at the fishbowl front desk manager. | 2027
83458 |  | (CN) JLL-001 Main Lodge Building (JL-1 Main Lodge) | LMAC | Replace doorknobs with ones that don't require tight grasping, pinching, or twisting of rest to operate as per ADAABAG Section 309.4; 34" x 78" Solid Core - Wood, Standard Interior Door, Lockset Hardware, Painted With wood Grill measuring 26 inches wide and 18 Inches tall. Located at the Bellman's closet | 2027
83458 |  | (CN) JLL-001 Main Lodge Building (JL-1 Main Lodge) | LMAC | Replace door handle located at the float’s office. Door to the guest business center, executive offices, and other employee offices throughout the main floor, along with mold employees access doors throughout the building have knob style hardware that requires tight grasping and twisting of rest to operate. Need replacing according to ADAABAG Section 309.4. | 2027
83458 |  | (CN) JLL-001 Main Lodge Building (JL-1 Main Lodge) | LMAC | Replace doorknobs with ones that don't require grasping, pinching, or twisting of the wrist to operate as per ADAABAG Section 309.4; 36" x 80" Solid Core - Wood, Glazed Interior Door, Lockset Hardware, Painted Full lite door. Located At the room division managers office. | 2027
83458 |  | (CN) JLL-001 Main Lodge Building (JL-1 Main Lodge) | LMAC | Adjust threshold level so that the floor level changes a maximum of 1/2" at accessible doors and beveled with a slope no greater than 1/2 as per code ADAABAG Section 404.2.5 36" x 80" Solid Core - Wood, Glazed Interior Door, Lockset Hardware, Painted Full lite door. Located entry into executive offices | 2027
83458 |  | (CN) JLL-001 Main Lodge Building (JL-1 Main Lodge) | LMAC | Replace handle hardware so that handles, pulls, latches, locks, or other operating devices on doors have a shape that is easy to grasp with one hand and not require tight grasping, tight pinching or twisting of the wrist to operate as per code ADAABAG Section 309.4, 36" x 78" Solid Core - Wood, Dutch Style Door, Lockset hardware, Painted Located at the vault office. | 2027
83458 |  | (CN) JLL-001 Main Lodge Building (JL-1 Main Lodge) | LMAC | Replace doorknobs with ones that don't require grasping, pinching, or twisting or the wrist to operate as per ADAABAG Section 309.4; 30" x 80" Hollow Core - Wood, Standard Interior Door, Lockset Hardware, Painted With wood grill measuring 20" x 20". Located between the box office and the vault. | 2027
83458 |  | (CN) JLL-001 Main Lodge Building (JL-1 Main Lodge) | LMAC | Adjust Threshold level changes at entry doors to (Mural Room) have a vertical change of slightly greater than 1/2 inch (wood). threshold needs replacing according to ADAABAG Section 404.2.5.70" x 80" Wood, Standard Interior Door, Self-Closer, Pull Handle and Push Plate, Stained Double door with kick plates. Upper single pane glazing measuring 24 inches wide and 29 inches tall in each door. Lower single pane glazing measuring 24 inches wide and 25 inches tall in each door. (1) Located at the entrance to Trappers’ Room from the west upper lobby.70" x 80" Wood, Standard Interior Door, Self-Closer, Pull Handle and Push Plate, Stained Double door with kick plates. Upper single pane glazing measuring 24 inches wide and 29 inches tall in each door. Lower single pane glazing measuring 24 inches wide and 25 inches tall in each door Located at the entrance to the mural room from the west upper lobby | 2027
83458 |  | (CN) JLL-001 Main Lodge Building (JL-1 Main Lodge) | LMAC | Adjust Threshold level at the business center entry door and entry door into executive offices have a threshold greater than 1/2-inch vertical change. threshold needs replacing according to ADAABAG Section 404.2.5. 70" x 80" Wood, Standard Interior Door, Self-Closer, Pull Handle and Push Plate, Stained Double door with kick plates. Upper single pane glazing measuring 24 inches wide and 29 inches tall in each door. Lower single pane glazing measuring 24 inches wide and 25 inches tall in each door. | 2027
83458 |  | (CN) JLL-001 Main Lodge Building (JL-1 Main Lodge) | LMAC | Adjust door closer so that from an open position of 90 degrees, the door will take at least 5 seconds to move to a point 12 degrees from the latch, measured to the leading edge of the door. Located at the entrance to the mural room from the west upper lobby.70" x 80" Wood, Standard Interior Door, Self-Closer, Pull Handle and Push Plate, Stained Double door with kick plates. Upper single pane glazing measuring 24 inches wide and 29 inches tall in each door. Lower single pane glazing measuring 24 inches wide and 25 inches tall in each door. | 2027
83458 |  | (CN) JLL-001 Main Lodge Building (JL-1 Main Lodge) | LMAC | Adjust door closer so that the force required to push or pull open the door is a maximum of 5 lbs. on doors at entry to Mural room and pioneer Grille;70" x 80" Wood, Standard Interior Door, Self-Closer, Pull Handle and Push Plate, Stained Double door with kick plates. Upper single pane glazing measuring 24 inches wide and 29 inches tall in each door. Lower single pane glazing measuring 24 inches wide and 25 inches tall in each door. | 2027
83458 |  | (CN) JLL-001 Main Lodge Building (JL-1 Main Lodge) | LMAC | Adjust door closer so that the sweep period of the closer adjusted so that from an open position of 90 degrees, the door will take at least 5 seconds to move to a point 12 degrees from the latch, measured to the leading edge of the door as per code ADAABAG Section 404.2.8.1,70" x 80" Wood, Standard Interior Door, Self-Closer, Pull Handle and Push Plate, Stained Double door with kick plates. Upper single pane glazing measuring 24 inches wide and 29 inches tall in each door. Lower single pane glazing measuring 24 inches wide and 25 inches tall in each door. Located at the entrance to the mural room from the west upper lobby | 2027
83458 |  | (CN) JLL-001 Main Lodge Building (JL-1 Main Lodge) | LMAC | Replace doorknobs with ones that don't require grasping, pinching, or twisting to operate as per ADAABAG Section 309.4; 24" x 80" Hollow Core - Wood, Standard Interior Door, Lockset Hardware, Factory Finish Located at the Teton T-shirt shop dressing room. | 2027
83458 |  | (CN) JLL-001 Main Lodge Building (JL-1 Main Lodge) | LMAC | Replace doorknobs with ones that don't require grasping, pinching, or twisting of the wrist to operate. In accordance with ADAABAG Section 309.4 the knobs need replacing. Located at apparel shop storage rooms one and two at apparel shop dressing room. The doorway to the dressing room; 24" x 84" Wood, Standard Interior Door, Lockset Hardware, Factory Finish Wood louvered door. | 2027
83458 |  | (CN) JLL-001 Main Lodge Building (JL-1 Main Lodge) | LMAC | Add door pulls to Accessible Stall door pulls that must be provided on both sides of the door. Add ADA Stall Door Hardware per ADAABAG 604.8.1.2, 404.2.7, 110" x 84" x 58" Plastic Laminate, Fabricated Toilet Partition With (1) 32 x 58 inch door and (1) 22 x 58“door. Located in the men’s restroom near the Trappers Room entry. | 2027
83458 |  | (CN) JLL-001 Main Lodge Building (JL-1 Main Lodge) | LMAC | Replace Accessible Stall Grab Bar required length of the grab bar on the side wall next to the toilet needs to a minimum of 42". Replace Grab Bar per ADAABAG 604.5.1, 1.5" diameter x 24" Stainless Steel, Grab Bar Located in the women’s and men’s restroom near the Trappers Room entry | 2027
83458 |  | (CN) JLL-001 Main Lodge Building (JL-1 Main Lodge) | LMAC | Add door pulls to Accessible Stall door pulls must be provided on both sides of the door. Add ADA Stall Door Hardware per ADAABAG 604.8.1.2, 404.2.7, 104" x 84" x 56" Plastic Laminate, Fabricated Toilet Partition One 32 x 58 inch door. Three 22 x 58“ door. Located in the women’s restroom near the Trappers Room entry | 2027
83458 |  | (CN) JLL-001 Main Lodge Building (JL-1 Main Lodge) | LMAC | Replace ADA door hardware so that handles, pulls, latches or other operating devices on accessible stall doors have a shape that is easy to grasp with one hand and not require tight grasping, tight pinching or twisting of the wrist to operate per ADAABAG 309.4, 61" x 84" x 71" Solid Surface, Fabricated Toilet Partition With one door measuring 36 inches wide and 54 inches tall. Located at the ADA stall in second floor men’s & women's restrooms. | 2027
83458 |  | (CN) JLL-001 Main Lodge Building (JL-1 Main Lodge) | LMAC | Replace grab bar with on that the Length of Grab Bar on the side wall next to the toilet a minimum of 42". Replace Grab Bar per 604.5.1, 1.5" diameter x 46" Stainless Steel, Grab Bar Continuous corner grab bar. Located in ADA stall in the second-floor men’s restroom and women’s restroom. | 2027
83458 |  | (CN) JLL-001 Main Lodge Building (JL-1 Main Lodge) | LMAC | Add proper hardware so that the stall door pulls provided on both sides of the accessible stall door as per ADAABAG 604.8.1.2, 404.2.7, 64" x 84" x 43" Solid Surface, Fabricated Toilet Partition With one door measuring 36 inches wide and 54 inches tall. Located at the ADA stall in second floor women’s restroom | 2027
83458 |  | (CN) JLL-001 Main Lodge Building (JL-1 Main Lodge) | LMAC | Replace grab bar at Accessible Toilet in each accessible guestroom bathroom to have a horizontal grab bar along the wall behind the toilet that is at least 36" long and mounted 33"-36" above the floor for stabilization and assistance. Replace Grab Bar per ADAABAG 604.5.2, 1.5" diameter Stainless Steel, Grab Bar 24". Located in guestroom bathroom 11. | 2027
83458 |  | (CN) JLL-001 Main Lodge Building (JL-1 Main Lodge) | LMAC | Adjust Accessible Bathroom Grab Bars so the gap between wall and the inside face of the grab bar required to be exactly 1 1/2" to accommodate persons with disabilities who rest their forearms on the bars for stabilization so arm cannot accidentally slip. Adjust Grab Bar per ADAABAG 609.3, 1.5" diameter Stainless Steel, Grab Bar 24". Located in guestroom bathroom 18. | 2027
83458 |  | (CN) JLL-001 Main Lodge Building (JL-1 Main Lodge) | LMAC | Replace 36" grab bar along the side wall of the Water Closet that requires a grab bar on the side wall to be a minimum length of 42". Replace Grab Bar per ADAABAG 604.5.1, 1.5" diameter Stainless Steel, Grab Bar 36". Located in guestroom bathroom 18, and add Grab Bar to the side wall of the toilet in guest room 11. | 2027
83458 |  | (CN) JLL-001 Main Lodge Building (JL-1 Main Lodge) | LMAC | Add self-closer to accessible Stall that is required to be self-closing. Replace ADA Stall Door per ADAABAG 604.8.1.2, 60" x 84" x 56" Fabricated Toilet Partition With one 36 x 58“ door. Located in the women’s and men’s restroom on the main level. | 2027
83458 |  | (CN) JLL-001 Main Lodge Building (JL-1 Main Lodge) | LMAC | Replace the 30" grab bar behind the Water Closet that is required to have a horizontal grab bar along the wall behind the water closet that is at least 36" long and mounted 33"-36" above the floor for stabilization and assistance. Replace Grab Bar per ADAABAG 604.5.2, 1.5" diameter Stainless Steel, Grab Bar 30", Located in guestroom 18 | 2027
83458 |  | (CN) JLL-001 Main Lodge Building (JL-1 Main Lodge) | LMAC | Adjust grab bar at accessible Bathroom Grab Bars so the gap between wall and the inside face of the grab bar required to be exactly 1 1/2" to accommodate persons with disabilities who rest their forearms on the bars for stabilization so arm cannot accidentally slip. Adjust Grab Bars per ADAABAG 609.3, 1.5" diameter x 48" Stainless Steel Located in guestroom 18 | 2027
83458 |  | (CN) JLL-001 Main Lodge Building (JL-1 Main Lodge) | LMAC | Adjust Cab elevator door so that the reopening device keep the door open for at least 20 seconds as per ADAABAG Section 407.3.3.3; 68" x 78" x 84" Passenger Elevator, Otis brand elevator, 3000-pound capacity, hydraulic elevator includes decorative wall finish, wallpaper above a 4-inch diameter chair rail and 32-inch tall wood paneling along bottom. Elevator includes a one by six baseboard trim at interior of cab. Elevator includes double acting stainless steel sliding doors. Stainless steel service panel, service to three floors. Assembly includes sliding doors at each of the three floors, stainless steel. Located at the guest elevator. | 2027
83458 |  | (CN) JLL-001 Main Lodge Building (JL-1 Main Lodge) | LMAC | Adjust height so that the flush control mounted no higher than 44" above the floor as per code ADAABAG 605.4, Porcelain, Urinal, Tankless, with Manual Handle Flush Valve Floor mounted. Located in men’s restroom on the main floor. | 2027
83458 |  | (CN) JLL-001 Main Lodge Building (JL-1 Main Lodge) | LMAC | Adjust the toilet so that the center of the water closet (toilet) 16"-18" from the closest wall as per code ADAABAG Section 604.2, 18" x 26" Porcelain, Water Closet, Tankless, Wall Mounted, with Manual Handle Flush Valve Koehler. located in the men's and women's ADA stalls in the restrooms on the main level. | 2027
83458 |  | (CN) JLL-001 Main Lodge Building (JL-1 Main Lodge) | LMAC | Adjust the flushing hardware so that the flush if hand controlled, it is located on the open side of the water closet as per code ADAABAG Section 604.6, 18" x 26" Porcelain, Water Closet, Tankless, Wall Mounted, with Manual Handle Flush Valve Koehler. Located at the men's ADA stall in the main level restroom. | 2027
83458 |  | (CN) JLL-001 Main Lodge Building (JL-1 Main Lodge) | LMAC | Adjust so that the height of the accessible water closet (toilet) 17" to 19" when measured from the floor to the top of the toilet seat as per code ADAABAG Section 604.4, 18" x 26" Porcelain, Water Closet, Tankless, Wall Mounted, with Manual Handle Flush Valve Koehler. located in the ADA stalls of both the men's and the women's restrooms located on the main level. | 2027
83458 |  | (CN) JLL-001 Main Lodge Building (JL-1 Main Lodge) | LMAC | Add protective covering to drainpipes so that the lavatory in each accessible guestroom bathroom have drain and hot water pipes that are insulated or otherwise configured to protect against contact as per code Department of Justice, ADAABAG, 14" x 10" x 8" Porcelain, Lavatory, in ADA guest restroom 18 | 2027
83458 |  | (CN) JLL-001 Main Lodge Building (JL-1 Main Lodge) | LMAC | Relocate visual alarms so that them are placed 80" above the floor or 6" below the ceiling, whichever is lower as per code ADAABAG Section 702.1, Ceiling Mounted, Fire Alarm with Strobe Located in engendering shop carpentry, and on the west wall of the boiler room. One located in the wrangler room. One in the Homestead room. One in the prospector room. Three in the hallway between the prospector room and the Explorers Room and one located in Explorer’s pantry west. To located in the west upper lobby one on the north end and one on the south end. One on the south wall near the east end of the hallway to service rooms and Eagles Nest on the third floor. | 2027
83458 |  | (CN) JLL-001 Main Lodge Building (JL-1 Main Lodge) | LMCO | Verify tempered glazing. There is no temperature glazing labeled in any of the glass panes in the storefront system. Wood, Interior Window, Stained Storefront wall on the northeast corner of the newsstand. (~12 lf) | 2027
83458 |  | (CN) JLL-001 Main Lodge Building (JL-1 Main Lodge) | LMCO | Verify tempered glazing. There is no temperature grazing labeled adjacent to the door; 48' Wood, Interior Window fixed glazing Storefront wall on south and west walls of Fish Bowl Front Desk Manager. | 2027
83458 |  | (CN) JLL-001 Main Lodge Building (JL-1 Main Lodge) | LMCO | Verify glazing adjacent the door opening is tempered. Wood, Interior Window fixed glazing Storefront wall on west wall of Division Manager. | 2027
83458 |  | (CN) JLL-001 Main Lodge Building (JL-1 Main Lodge) | LMCO | Remove items beneath stairs as no storage beneath these stairs is allowed under stairway per code. Remove items currently stored in this location and post preventative notice. Concrete, Interior Stair Construction Assembly, Straight-Run Design, with Steel Pipe Railing, with closed riser 6’-0" wide concrete stairs, 8 treads @ 11", 9 risers @ 8", with 3" grip strip on edge of treads (48 LF), with 6’x3’ landing at top of stair, 2" metal railing both sides 20LF. Located at north end of boiler room. | 2027
83458 |  | (CN) JLL-001 Main Lodge Building (JL-1 Main Lodge) | LMCO | Replace Missing bottom furnace cover of 36" x 36" x 24" Ceiling Mounted, Gas Fired Space Heater Janitor brand, with 8-inch exhaust flue through ceiling (55 LF), Located centered over engineering department shop room. | 2027
83458 |  | (CN) JLL-001 Main Lodge Building (JL-1 Main Lodge) | LMCO | Replace broken latches on electrical panel cover as per code NEC Code Reference 408.38 Located in Engineering office 3 dispatch, panels EDP 1 | 2027
83458 |  | (CN) JLL-001 Main Lodge Building (JL-1 Main Lodge) | LMCO | Install proper breaker ties in the panel VP five as per code 2010 NEC Code Reference 240.15 (B)(1), Metal Panel Box, Electrical Sub Panel, Square D brand, with, 14 Breakers, 100 Amp/3 Wire System Panel Dp 5, located in the back hall main, along the wall that shares the hall and the dishwashing area. | 2027
83458 |  | (CN) JLL-001 Main Lodge Building (JL-1 Main Lodge) | LMCO | Repair broken latch as per code NEC Code Reference 408.38, 14" x 38" Metal Panel Box, Electrical Sub Panel, Square D brand, with, 42 Breakers, 225 Amp/3 Wire System EDP 6 panel. Located along the east wall of the compressor room | 2027
83458 |  | (CN) JLL-001 Main Lodge Building (JL-1 Main Lodge) | LMCO | Replace missing latch as per code NEC Code Reference 408.38, 20" x 35" Metal Panel Box, Electrical Sub Panel, Square D brand, with, 30 Breakers, 225 Amp/3 Wire System Panel h4. Located in the Convention Storage 2, along the north wall on the northwest corner on the column | 2027
83458 |  | (CN) JLL-001 Main Lodge Building (JL-1 Main Lodge) | LMCO | Label electrical panel as per code 110.22, 20" x 74" Metal Panel Box, Electrical Sub Panel, Square D brand, with, 42 Breakers, 400 Amp/3 Wire System Panel El section 1. Has main breaker disconnect that is 400 amp. Located along the south wall of the north generator room | 2027
83458 |  | (CN) JLL-001 Main Lodge Building (JL-1 Main Lodge) | LMCO | Secure electrical line in conduit to protect wire from physical damage as per code NEC (334.15 B), Electrical Wiring Distribution Lines Yes the copper cable. 600 V. 45lf. Located along the south wall of the Explorers pantry west near the west entrance | 2027
83458 |  | (CN) JLL-001 Main Lodge Building (JL-1 Main Lodge) | LMCO | Install proper breaker ties as per code 2010 NEC Code Reference 240.15 (B)(1), 22" x 30" Metal Panel Box, Electrical Sub Panel, Square D brand, with, 30 Breakers, 225 Amp/3 Wire System Panel LP 1. Located along the south wall of the men's restroom hallway. | 2027
83458 |  | (CN) JLL-001 Main Lodge Building (JL-1 Main Lodge) | LMCO | Replace cover so that the exposed wires will be covered as per code NEC Code Reference 408.38, 22" x 30" Metal Panel Box, Electrical Sub Panel, Square D brand, with, 30 Breakers, 225 Amp/3 Wire System Panel LP 1. Located along the south wall of the men's restroom hallway. | 2027
83458 |  | (CN) JLL-001 Main Lodge Building (JL-1 Main Lodge) | LMCO | Install proper knock out covers as per code 110.12 (Section A), 20" x 34" Metal Panel Box, Electrical Sub Panel, Square D brand, with, 42 Breakers, 225 Amp/4 Wire System Panel GL. Located along the west wall of the gift shop storage. | 2027
83458 |  | (CN) JLL-001 Main Lodge Building (JL-1 Main Lodge) | LMCO | Replace missing junction box cover on electrical Chase located in the compressor room along the west walk as per code 2010 NEC Code Reference 250.35.3, 4" x 48" x 4" Metal, Electrical Junction Box Located along the west wall of the compressor room. | 2027
83458 |  | (CN) JLL-001 Main Lodge Building (JL-1 Main Lodge) | LMCO | Replace broken latch on an electrical panel that is now converted to a junction box as per code NEC Code Reference 408.38, 12" x 16" Metal, Electrical Junction Box Located along the east wall the banquet storage room. | 2027
83458 |  | (CN) JLL-001 Main Lodge Building (JL-1 Main Lodge) | LMCO | Replace landing and handrail with landing and handrail that meet code requirements. | 2027
83458 |  | (CN) JLL-001 Main Lodge Building (JL-1 Main Lodge) | LMFS | Update to rated wall enclosure on sealed opening in west concrete wall in the boiler room. | 2027
83458 |  | (CN) JLL-001 Main Lodge Building (JL-1 Main Lodge) | LMFS | Add Fire Seal to Openings from fire sprinkler system into concrete boiler stair shaft. 12" Fixed Partition Cast in Place concrete wall. | 2027
83458 |  | (CN) JLL-001 Main Lodge Building (JL-1 Main Lodge) | LMFS | Adjust door as the Carpet impedes proper closure of guestroom doors 15, 17, 27, 29, 30, 32, 35, 38, 41; 34" x 80" Solid Core - Wood, Standard Interior Door, Self-Closer, Lockset Hardware, Painted. | 2027
83458 |  | (CN) JLL-001 Main Lodge Building (JL-1 Main Lodge) | LMFS | Replace missing smoke seal at guestroom 11; 36" x 80" Solid Core - Wood, Standard Interior Door, Self-Closer, Lockset Hardware, Painted. | 2027
83458 |  | (CN) JLL-001 Main Lodge Building (JL-1 Main Lodge) | LMFS | Install sprinkler fire suppression systems where not present throughout the whole building, especially the first floor Corridor and dishwashing room. | 2027
83458 |  | (CN) JLL-001 Main Lodge Building (JL-1 Main Lodge) | LMLS | Repair loose and detached door closer on exit door on the east side south hallway 36" x 84" Metal Divided Lite, Exterior Entrance Door, with Panic Hardware, Lockset with Key, Painted With self-closure, pull handle and 3 divided lite (25" x 11") metal mesh inlay. (1) Located on the east side of the Hallway to Rooms 37 - 38, | 2027
83458 |  | (CN) JLL-001 Main Lodge Building (JL-1 Main Lodge) | LMLS | Consult with IMR Fire Manager and Park Safety Officer to consider egress on the third-floor guest suites | 2027
83458 |  | (CN) JLL-001 Main Lodge Building (JL-1 Main Lodge) | LMLS | Add fire suppression elements and repair CMU block were required on third floor between residential hotel units. This includes active fire caulking at the top of CMU walls fire dampers at duct penetrations and ceiling all other pipe penetrations through wall. | 2027
83458 |  | (CN) JLL-001 Main Lodge Building (JL-1 Main Lodge) | LMLS | Remove sliding pin style lock so that it can't accidentally be locked impeding emergency egress; 32" x 80" Hollow Core - Metal, Standard Interior Door, Self-Closer, Pull Handle and Push Plate, Painted Located at the fire escape stairwell on the third floor | 2027
83458 |  | (CN) JLL-001 Main Lodge Building (JL-1 Main Lodge) | LMLS | Test for possible asbestos in the old gym walls; Gypsum Board, Interior Wall Covering Material Unpainted. 686 LF Located in rooms 1000: South Generator entry north and east wall, 1305: Retail Storeroom 1 on north wall and back offices. Also 1307: IT Servers, 2217: Gift Shop Storage, 2207: Teton Storage 1, 3107: Heron Attic Retail Storage south and west wall. | 2027
83458 |  | (CN) JLL-001 Main Lodge Building (JL-1 Main Lodge) | LMLS | Test Tile known for asbestos, 9" x 9" VCT, Interior Floor Covering Material, Factory Finish Located in floats office (54 SF), bellman closet (109 SF), and news stand storage (72 SF)) | 2027
83458 |  | (CN) JLL-001 Main Lodge Building (JL-1 Main Lodge) | LMLS | Patch holes in drywall in South Generator Room over entry; Drywall, Interior Ceiling Covering Material. | 2027
83458 |  | (CN) JLL-001 Main Lodge Building (JL-1 Main Lodge) | LMLS | Test gypsum for possible asbestos in South Generator Room; Drywall, Interior Ceiling Covering Material, Unfinished | 2027
83458 |  | (CN) JLL-001 Main Lodge Building (JL-1 Main Lodge) | LMLS | Install flexible gas supply line as per legis code, 36" x 36" x 24" Ceiling Mounted, Gas Fired Space Heater Janitor brand, with 8-inch exhaust flue through ceiling (55 LF), Located centered over engineering department shop room. | 2027
83458 |  | (CN) JLL-001 Main Lodge Building (JL-1 Main Lodge) | LMLS | Re-Secure the panel to the wall 20" x 26" Metal Panel Box, Electrical Sub Panel, Square D brand, with, 24 Breakers, 200 Amp/3 Wire System Located in the hallway to rooms 10 -17. Located in the hallway next to the housekeeping offices. | 2027
83458 |  | (CN) JLL-001 Main Lodge Building (JL-1 Main Lodge) | LMLS | Replace missing latch for electrical panel as per code NEC Code Reference 408, 20" x 48" Metal Panel Box, Electrical Sub Panel, Square D brand, with, 18 Breakers, 200 Amp/3 Wire System Located along the north wall in engineering office 3 dispatch Panel DP 1 | 2027
83458 |  | (CN) JLL-001 Main Lodge Building (JL-1 Main Lodge) | LMLS | Install proper breaker ties in the panel VP five as per code 2010 NEC Code Reference 240.15 (B)(1), Metal Panel Box, Electrical Sub Panel, Square D brand, with, 42 Breakers, 200 Amp/3 Wire System Banquets panel. Located in the hallway 1200 on the wall that separates the hall from the dishwashing area | 2027
83458 |  | (CN) JLL-001 Main Lodge Building (JL-1 Main Lodge) | LMLS | Add emergency lighting on all floors as the current emergency lighting is insufficient, throughout the building. | 2027
83458 |  | (CN) JLL-001 Main Lodge Building (JL-1 Main Lodge) | RMDM | Repaint wood window frames as they are past due; 160" x 35" Wood, Glazed Window, Stationary, Single Pane, Painted Divided into three sections of windowpanes 52 X 35. Secondary, removable window with same dimensions. Located on the west wall of engineering shop general maintenance and engineering hallway. | 2027
83458 |  | (CN) JLL-001 Main Lodge Building (JL-1 Main Lodge) | RMDM | Repaint Window Frames as they are past due; 81" x 158" Wood, Glazed Window, Awning, Safety Glass, Painted, with aluminum screen Each window has 12 panel sections. Dimension of 50" x 19" per section. Located on the east wall of laundry room. | 2027
83458 |  | (CN) JLL-001 Main Lodge Building (JL-1 Main Lodge) | RMDM | Repaint Window Frames as they are past due; 159" x 38" Wood, Glazed Window, Awning, Single Pane, Painted Each window has 3 panel sections. Dimension of 50" x 36" per section. One panel section has been removed for ventilation from two of the windows. Located on east wall of dishwashing room “Suds" | 2027
83458 |  | (CN) JLL-001 Main Lodge Building (JL-1 Main Lodge) | RMDM | Paint wood window as it is past due; 158" x 38" Wood, Glazed Window, Awning, Single Pane, Painted This section is divided up into three windows, measuring 50" x 35" each. Located on the west side of uniform room. | 2027
83458 |  | (CN) JLL-001 Main Lodge Building (JL-1 Main Lodge) | RMDM | Paint Window frames as they are past due; 158" x 38" Wood, Glazed Window, Awning, Single Pane, Painted Each window is divided into 3 panel sections. Dimension of 50" x 35" per section. The south window has two sections for ventilation. Located on the west side of purchasing storeroom. | 2027
83458 |  | (CN) JLL-001 Main Lodge Building (JL-1 Main Lodge) | RMDM | Paint window frames as they are past due; 52" x 38" Wood, Glazed Window, Awning, Single Pane, Painted Located on the north side of north elevator foyer (room 1508). | 2027
83458 |  | (CN) JLL-001 Main Lodge Building (JL-1 Main Lodge) | RMDM | Paint window frame as they are past due; 41" x 80" Wood, Glazed Window, Awning, Single Pane, Painted, with wood screen Located on the south side of the lower lobby. | 2027
83458 |  | (CN) JLL-001 Main Lodge Building (JL-1 Main Lodge) | RMDM | Paint window frames as they are past due; 45" x 52" Wood, Glazed Window, Awning, Single Pane, Painted, with wood screen Located on the north and east side of the elevator mechanical room. | 2027
83458 |  | (CN) JLL-001 Main Lodge Building (JL-1 Main Lodge) | RMDM | Repaint exterior door as it is past due; 35" x 84" Steel, Divided Lite, Exterior Entrance Door, with Self-Closing Device, Deadbolt and Door Handle, Painted Located on the north side of Stairwell South Entry Hall on ground level. | 2027
83458 |  | (CN) JLL-001 Main Lodge Building (JL-1 Main Lodge) | RMDM | Repaint exterior door as it is past due; 35" x 80" Steel, Divided Lite, Exterior Entrance Door, with Push Bar, Deadbolt and Door Handle, Painted Located on the south side of Stairwell South Entry Hall on ground level. | 2027
83458 |  | (CN) JLL-001 Main Lodge Building (JL-1 Main Lodge) | RMDM | Repaint exterior door as it is past due; 40" x 80" Wood, Divided Lite, Exterior Entrance Door, with Self-Closing Device, Lockset with Key, Painted Located on the south side of Engineering Shop 2 General Maintenance. | 2027
83458 |  | (CN) JLL-001 Main Lodge Building (JL-1 Main Lodge) | RMDM | Repaint exterior door as it is past due; 60" x 96" Wood, Exterior Entrance Door, Painted Double hung door with no hardware. Located on the east side of South Generator Room. | 2027
83458 |  | (CN) JLL-001 Main Lodge Building (JL-1 Main Lodge) | RMDM | Repaint exterior door as it is past due; 60" x 80" Wood, Exterior Entrance Door, Deadbolt, Painted Located on the east side of Engineering Office 1 Carpentry. | 2027
83458 |  | (CN) JLL-001 Main Lodge Building (JL-1 Main Lodge) | RMDM | Repaint exterior door as they are past due; 75" x 80" Metal, Exterior Entrance Door, Lever Handle, Painted A slider door. Located at Grease Storage. | 2027
83458 |  | (CN) JLL-001 Main Lodge Building (JL-1 Main Lodge) | RMDM | Repaint exterior door as it is past due; 64" x 80" Steel, Exterior Entrance Door, Deadbolt and Door Handle, Painted Double hung door. Located on the east side of room Stairwell Foyer Boiler/Accounting. | 2027
83458 |  | (CN) JLL-001 Main Lodge Building (JL-1 Main Lodge) | RMDM | Repaint exterior door as it is past due; 72" x 84" Wood, Exterior Entrance Door, Painted Double hung door, Located on the southeast corner of laundry room. | 2027
83458 |  | (CN) JLL-001 Main Lodge Building (JL-1 Main Lodge) | RMDM | Repaint exterior door as it is past due; 72" x 84" Wood, Exterior Entrance Door, with Panic Hardware, Painted Double hung door. Located in the main corridor entering the loading dock. | 2027
83458 |  | (CN) JLL-001 Main Lodge Building (JL-1 Main Lodge) | RMDM | Repaint door as it has begun to erode needs repainting.36" x 84" Hollow Core - Metal, Standard Interior Door, Lockset Hardware, Painted Located between convention storage one linens and stairwell north. Located at the top of the stairs for entry into retail storage garage. | 2027
83459 |  | (CN) JLL-300 General Manager House (JL-2 Manager's Resid) | DM | Replace fascia board along north end of structure, fascia board has been severely damaged by failing roof structure and water penetration. 2" X 14", Wood, Fascia Board, Painted, mounted at an angle, around entire perimeter of structure. 40 LF. | 2027
83460 |  | (CN) JLL-100 Cottage 101 - 119 (JL-3 M.U. (10) 101-119) | DM | Secure post to foundation located at room 101 4" x 4", Wood, Structural Support Post, Painted, Located at entry canopy of room 101. | 2027
83460 |  | (CN) JLL-100 Cottage 101 - 119 (JL-3 M.U. (10) 101-119) | DM | Remove landscaping bark from exterior siding at rooms at cottages 117, 119, & 101, 24" X 12", Exterior Siding Material, Lap, Painted, Asbestos lap shingle nailed to exterior. | 2027
83460 |  | (CN) JLL-100 Cottage 101 - 119 (JL-3 M.U. (10) 101-119) | DM | Replace missing gravel at 5% of roof area Tar & Gravel, Roof Finish, with 4" metal drip edge. | 2027
83460 |  | (CN) JLL-100 Cottage 101 - 119 (JL-3 M.U. (10) 101-119) | DM | Replace tar at critical joint locations on roof; Tar & Gravel, Roof Finish, with 4" metal drip edge. | 2027
83460 |  | (CN) JLL-100 Cottage 101 - 119 (JL-3 M.U. (10) 101-119) | DM | Replace rotting wood located at room 105 and 113, 2" X 6", Wood, Fascia Board, Painted, Located at perimeter of roof | 2027
83460 |  | (CN) JLL-100 Cottage 101 - 119 (JL-3 M.U. (10) 101-119) | LMAC | Reduce threshold height to be a maximum of 1/2" and a slope no greater than 1:2, as per ADAABAG Section 404.2.5. The main exterior entrance door to both accessible units in this building have a threshold rise of approximately 1 inch. Located at the entrance to both units 101 and 103. 36" x 80" Wood, Solid Core, Exterior Entrance Door, Deadbolt and Door Handle, Painted Metal clad. | 2027
83460 |  | (CN) JLL-100 Cottage 101 - 119 (JL-3 M.U. (10) 101-119) | LMAC | Adjust the grab bar at the accessible toilet in each accessible guestroom bathroom have a horizontal grab bar along the wall behind the toilet that is at least 36" long and mounted 33"-36" above the floor for stabilization and assistance as per code Department of Justice, ADAABAG 604.5.2, 2" diameter x 36" Stainless Steel, Grab Bar Located behind toilet unit 103. | 2027
83460 |  | (CN) JLL-100 Cottage 101 - 119 (JL-3 M.U. (10) 101-119) | LMAC | Install grab bar behind toilet in unit 101 bathroom so that it has a horizontal grab bar along the wall behind the toilet that is at least 36" long and mounted 33"-36" above the floor for stabilization and assistance as per code Department of Justice, ADAABAG 604.5.2, | 2027
83460 |  | (CN) JLL-100 Cottage 101 - 119 (JL-3 M.U. (10) 101-119) | LMAC | Adjust height of the rod in Accessible Guest Rooms and Suites-Closet Rod/Shelf mounted between 40" and 48 as per Department of Justice, ADAABAG located in unit 103 | 2027
83460 |  | (CN) JLL-100 Cottage 101 - 119 (JL-3 M.U. (10) 101-119) | LMAC | Install wrap pipes to insulate the lavatory in each accessible guestroom bathroom so that the drain and hot water pipes are configured to protect against contact as per ADAABAG Section 606.5 14" x 12" Porcelain, Lavatory, Drop-in-Countertop located in unit 103 | 2027
83460 |  | (CN) JLL-100 Cottage 101 - 119 (JL-3 M.U. (10) 101-119) | LMAC | Adjust the thermostats that are 52" above finished floor so that HVAC controls in accessible guestrooms placed a maximum of 48” to the highest operating mechanism if the reach is unobstructed as per ADAABAG Section 308.2.1 308.2.2 located in both the ADA bedrooms of unit 101 and 103. | 2027
83460 |  | (CN) JLL-100 Cottage 101 - 119 (JL-3 M.U. (10) 101-119) | LMCO | Label electrical panel as per code 110.22, 12" x 30" Metal Panel Box, Main Service Panel, Square D brand, with, 30 Breakers, 200 Amp/3 Wire System With main service disconnect breaker at 200 amp. | 2027
83460 |  | (CN) JLL-100 Cottage 101 - 119 (JL-3 M.U. (10) 101-119) | LMCO | Replace outlets under counter refrigerators are plugged into must be GFCI, within 5 ft. of water source as per 210.8(A) Dwelling units, | 2027
83460 |  | (CN) JLL-100 Cottage 101 - 119 (JL-3 M.U. (10) 101-119) | LMLS | Install knockout covers as per NEC Code Reference 408.38, 8" x 10" Metal Panel Box, Electrical Sub Panel, Square D brand, with 6 Breakers, 100 Amp/3 Wire System Located on the west end of the building | 2027
83461 |  | (CN) JLL-101 Cottage 121 - 127 (JL-4 M.U. (4)) | DM | Repair water damage at west elevation where roof meets wall, 2" X 6", Wood Framing, Exterior Wall Frame Assembly, @ 16" O. C., with plywood sheeting and rolled insulation | 2027
83461 |  | (CN) JLL-101 Cottage 121 - 127 (JL-4 M.U. (4)) | DM | Investigate mold in 127A, Drywall, Interior Ceiling Covering Material, Painted Unpainted in 127A. Located throughout building. | 2027
83461 |  | (CN) JLL-101 Cottage 121 - 127 (JL-4 M.U. (4)) | LMCO | Install conduit for exposed wiring as per code NEC Article 334.15(B), 12" x 30" Metal Panel Box, Main Service Panel, Square D brand, with, 30 Breakers, 200 Amp/3 Wire System With a main single breaker disconnect at 200 amp. Located in the storage room | 2027
83462 |  | (CN) JLL-102 Cottage 129 - 143 (JL-5 M.U. (8) 129-143) | CRDM | Replace as it is beyond its useful life: 8" x 8" Tile - Ceramic, Interior Wall Covering Material, With ceramic wall mounted soap dish. Located around tub/shower in bathrooms throughout | 2027
83462 |  | (CN) JLL-102 Cottage 129 - 143 (JL-5 M.U. (8) 129-143) | DM | Replace rotting wood on exterior corner where wall meets roof on West elevation, 2" X 4", Wood Framing, Exterior Wall Frame Assembly, @ 16" O. C., with plywood sheeting and rolled insulation. | 2027
83462 |  | (CN) JLL-102 Cottage 129 - 143 (JL-5 M.U. (8) 129-143) | DM | Remove landscaping bark in contact with siding. 24" X 12", Exterior Siding Material, Lap, Painted, Asbestos lab shingle mailed to exterior, Located around northeast corner of structure. | 2027
83462 |  | (CN) JLL-102 Cottage 129 - 143 (JL-5 M.U. (8) 129-143) | DM | Replace missing gravel where work was done on touring gravel roof, Tar & Gravel, Roof Finish, with 6" metal drip edge, Located above rooms 137 and 139. | 2027
83462 |  | (CN) JLL-102 Cottage 129 - 143 (JL-5 M.U. (8) 129-143) | LMCO | Replace standard 3-wire receptacle located behind refrigerator in each room, currently the outlet is tied to the GFCI located at the sink as per N.E.C. code 210.8(A) Dwelling units, Grounded, Standard 3-Wire Receptacle Located throughout the building | 2027
83463 |  | (CN) JLL-103 Cottage 100 - 114 & 301-315 (JL-6 M.U. (16)) | DM | Replace damaged and warped boards at canopy (3" x 6") at cottages 102, 108, & 110; 70" x 96" Wood, Canopy Construction Sunshade, Painted. Constructed with 3" x 6" sides, and (12) 1" x 8" slats each at (6 LF) placed at 45 degrees. a 1" x 4" strip at 4.5 LF long is located at the center. With 3/4" bolt hardware at either side. Located at West side taller entries. (2 per cottage) | 2027
83463 |  | (CN) JLL-103 Cottage 100 - 114 & 301-315 (JL-6 M.U. (16)) | LMAC | Adjust threshold so the floor level changes are a maximum of 1/2" and with a beveled slope no greater than 1:2; as per ADAABAG Section 404.2.5; 34" x 78" Metal, Exterior Entrance Door, Deadbolt and Door Handle, Painted Located at unit entries 100, 102, | 2027
83463 |  | (CN) JLL-103 Cottage 100 - 114 & 301-315 (JL-6 M.U. (16)) | LMAC | Adjust Closet Rod & shelf Height to be between 40" to 48”; as per Department of Justice ADAABAG; 41" x 83" x 24" Wood, Closet - Built Out With closet doors (2 @ 16x80) in cottages 100 & 102. | 2027
83463 |  | (CN) JLL-103 Cottage 100 - 114 & 301-315 (JL-6 M.U. (16)) | LMAC | Replace grab bar adjacent to the water closet with one that is at least 42" long and mounted 33"-36" above the floor; per Department of Justice, ADAABAG 604.5.1; Stainless Steel, Grab Bar 36" grab bar next to water closet, located in bathrooms of cottages 100 & 102 | 2027
83463 |  | (CN) JLL-103 Cottage 100 - 114 & 301-315 (JL-6 M.U. (16)) | LMAC | Add grab bars behind the water closet that are at least 36" long and mounted 33"-36" above the floor; per Department of Justice, ADAABAG 604.5.2 in bathrooms of cottages 100 & 102. | 2027
83463 |  | (CN) JLL-103 Cottage 100 - 114 & 301-315 (JL-6 M.U. (16)) | LMAC | Add horizontal grab bars that are 24" long at the foot of the tub, per Department of Justice, ADAABAG 607.4.1.2 in bathroom of cottages 100 & 102 | 2027
83463 |  | (CN) JLL-103 Cottage 100 - 114 & 301-315 (JL-6 M.U. (16)) | LMAC | Add horizontal grab bar that are at least 12" long at the head of the tub, per Department of Justice, ADAABAG 607.4.2.3 in bathroom of cottages 100 & 102. | 2027
83463 |  | (CN) JLL-103 Cottage 100 - 114 & 301-315 (JL-6 M.U. (16)) | LMAC | Add horizontal grab bar so that there are two on the side of the tub that are at least 24" long (one high and one low) per Department of Justice, ADAABAG 607.4.2.1 in bathrooms of cottages 100 & 102. | 2027
83463 |  | (CN) JLL-103 Cottage 100 - 114 & 301-315 (JL-6 M.U. (16)) | LMAC | Replace tub diverter so that it can be turned on and off easily and are operable and usable with one hand, without tight grasping, pinching, or twisting of the wrist as per code Department of Justice, ADAABAG 309.4, Located in bathroom of guestroom 100 & 102 | 2027
83463 |  | (CN) JLL-103 Cottage 100 - 114 & 301-315 (JL-6 M.U. (16)) | LMAC | Add adjustable height hand-held shower wand with at least 59" long hose, as per Department of Justice, ADAABAG 607.6 in bathroom of cottages 100 & 102. | 2027
83463 |  | (CN) JLL-103 Cottage 100 - 114 & 301-315 (JL-6 M.U. (16)) | LMAC | Add drain and hot water pipe insulation protection, per Department of Justice, ADAABAG on pipes below sinks in bathrooms of cottages 100 & 102. | 2027
83463 |  | (CN) JLL-103 Cottage 100 - 114 & 301-315 (JL-6 M.U. (16)) | LMCO | Protect electrical wires in conduit as they leave the electrical panel and before they enter the wall at panel in vending area; per NEC Article 334.15(B) 12 Gauge Wire, Electrical Wiring Distribution Lines, (about 4 LF) | 2027
83464 |  | (CN) JLL-104 Cottage 116 - 130 & 317-331 (JL-7 M.U. (16)) | DM | Replace missing gravel on roof (approximately 4%); Tar & Gravel, Roof Finish with 6" metal drip edge Located at entire roof. | 2027
83466 |  | (CN) JLL-106 Cottage 300 - 310 & 501-511 (JL-9 M.U. (12)) | DM | Replenish missing gravel (approximately 5%) Tar & Gravel, Roof Finish with 6" metal drip edge Located at entire roof | 2027
83466 |  | (CN) JLL-106 Cottage 300 - 310 & 501-511 (JL-9 M.U. (12)) | LMAC | Adjust threshold so the floor level changes are a maximum of 1/2" and with a beveled slope no greater than 1:2; as per ADAABAG Section 404.2.5; 34" x 78" Metal, Exterior Entrance Door, Deadbolt and Door Handle, Painted Located at unit entries 300 & 302. | 2027
83466 |  | (CN) JLL-106 Cottage 300 - 310 & 501-511 (JL-9 M.U. (12)) | LMAC | Replace grab bar adjacent to the water closet with on that is at least 42" long and mounted horizontally between 33" - 36" above the floor, per Department of Justice, ADAABAG 604.5.1 in bathroom of cottages 300 & 302 | 2027
83466 |  | (CN) JLL-106 Cottage 300 - 310 & 501-511 (JL-9 M.U. (12)) | LMAC | Add grab bars behind the water closet that are at least 36" long and mounted 33"-36" above the floor; per Department of Justice, ADAABAG 604.5.2 in bathrooms of cottages 300 & 302. | 2027
83466 |  | (CN) JLL-106 Cottage 300 - 310 & 501-511 (JL-9 M.U. (12)) | LMAC | Add horizontal grab bar so that there are two on the side of the tub that are at least 24" long (one high and one low) per Department of Justice, ADAABAG 607.4.2.1 located in the bathroom of cottages 300 & 3022. | 2027
83466 |  | (CN) JLL-106 Cottage 300 - 310 & 501-511 (JL-9 M.U. (12)) | LMAC | Replace shower diverter that is easy to turn on and off easily and can be operated and useable with one hand, without tight grasping, pinching, or twisting of the wrist, per Department of Justice, ADAABAG 309.4; in bathroom of cottages 300 & 302. | 2027
83466 |  | (CN) JLL-106 Cottage 300 - 310 & 501-511 (JL-9 M.U. (12)) | LMAC | Add horizontal grab bars that are 24" long at the foot of the tub, per Department of Justice, ADAABAG 607.4.1.2 in bathroom of cottages 300 & 302. | 2027
83466 |  | (CN) JLL-106 Cottage 300 - 310 & 501-511 (JL-9 M.U. (12)) | LMAC | Add horizontal grab bar that are at least 12" long at the head of the tub, per Department of Justice, ADAABAG 607.4.2.3 in bathroom of cottages 300 & 302. | 2027
83466 |  | (CN) JLL-106 Cottage 300 - 310 & 501-511 (JL-9 M.U. (12)) | LMAC | Add pipe insulation so that the lavatory in each accessible guestroom bathroom have drain and hot water pipes that are insulated or otherwise configured to protect against contact as per code Department of Justice, ADAABAG, Located in the bathroom of cottages 300 & 302 | 2027
83467 |  | (CN) JLL-107 Cottage 312 - 322 & 513-523 (JL-10 M.U. (12)) | DM | Replace missing gravel (approximately 5%) Tar & Gravel, Roof Finish, with 6" metal drip edge Located at entire roof | 2027
83468 |  | (CN) JLL-108 Cottage 324 - 330 & 529-535 (JL-11 M.U. (8)) | DM | Repair and replace damaged and/or missing shingles throughout building, 5%, 24" X 12", Exterior Siding Material, Lap, Painted, Asbestos lap shingle mailed to exterior, Located around exterior of building | 2027
83468 |  | (CN) JLL-108 Cottage 324 - 330 & 529-535 (JL-11 M.U. (8)) | DM | Check for the presence of asbestos siding, 24" X 12", Exterior Siding Material, Lap, Painted, Asbestos lap shingle nailed to exterior, Located around exterior of building | 2027
83468 |  | (CN) JLL-108 Cottage 324 - 330 & 529-535 (JL-11 M.U. (8)) | DM | Replace flashing where the roof meets wall to prevent water from running down wall. Tar & Gravel, Roof Finish with 6" metal drip edge Located on east and west elevations. | 2027
83468 |  | (CN) JLL-108 Cottage 324 - 330 & 529-535 (JL-11 M.U. (8)) | DM | Repaint drip edge behind sunshades on West and East elevations (104 LF) | 2027
83468 |  | (CN) JLL-108 Cottage 324 - 330 & 529-535 (JL-11 M.U. (8)) | DM | Remove and replace molded caulking with mold resistant caulk, Located around tub/shower in bathrooms throughout. | 2027
83468 |  | (CN) JLL-108 Cottage 324 - 330 & 529-535 (JL-11 M.U. (8)) | DM | Replace rotten wood on sunshade canopies located on east and west elevations, Sunshade canopy components Small; (5) 4x4 posts and post anchors at 7’-4", 4x8 beam (37 linear feet), 3x6 joists (17 linear feet), 2x6 box frames (126 linear feet), 1 x 8 slats (241 linear feet), 2x4 and 3" log screen walls (5’-8" tall x 20’ linear feet), 16 joist hangers, painted. | 2027
83468 |  | (CN) JLL-108 Cottage 324 - 330 & 529-535 (JL-11 M.U. (8)) | LMCO | Install new GFCI for the nonfunctioning one as per code 210.8(A) Dwelling units, Push Reset, GFCI Protected Receptacle One located in the bathroom of unit 328 | 2027
83469 |  | (CN) JLL-109 Cottage 332 - 346 & 537- 551 (JL-12 M.U. (16)) | DM | Repair or replace damaged panels at 30 locations around perimeter of the structure and at building corners. 24" x 12" Fiber Cement Siding, Exterior Siding Material, Lap, Painted With asbestos fibers | 2027
83469 |  | (CN) JLL-109 Cottage 332 - 346 & 537- 551 (JL-12 M.U. (16)) | DM | Install latches on Ice room windows 32" x 54" Wood, Glazed Window, Double Hung, Single Pane, Painted, with wood screen. | 2027
83469 |  | (CN) JLL-109 Cottage 332 - 346 & 537- 551 (JL-12 M.U. (16)) | DM | Repair dry rotted fascia located on East side of structure at unit 537. 2" x 6" Wood, Fascia Board Painted. (14 LF) | 2027
83469 |  | (CN) JLL-109 Cottage 332 - 346 & 537- 551 (JL-12 M.U. (16)) | DM | Replace missing gravel approximately 15%. Tar & Gravel, Roof Finish with 6" metal drip edge located at entire roof. | 2027
83469 |  | (CN) JLL-109 Cottage 332 - 346 & 537- 551 (JL-12 M.U. (16)) | DM | Replace water heater vault cover as its past end of useful life.64" x 180" Concrete, Utility Vault With wood plank cover. Located beneath ice room. (80 SF) | 2027
83469 |  | (CN) JLL-109 Cottage 332 - 346 & 537- 551 (JL-12 M.U. (16)) | LMCO | Label panel as per N.E.C. code 110.22. 12" X 34", Metal Panel Box, Electrical Sub Panel, Square D brand, with, 40 Breakers, 200 Amp/3 Wire System, Located on the north end of the building the electrical cabinet. | 2027
83469 |  | (CN) JLL-109 Cottage 332 - 346 & 537- 551 (JL-12 M.U. (16)) | LMCO | Install 2" conduit (4 LF) covering for electric lines exiting the top of the electrical panel to ensure safety as per code NEC Article 334.15 12" X 34", Metal Panel Box, Electrical Sub Panel, Square D brand, with, 40 Breakers, 200 Amp/3 Wire System, with 200-amp main breaker, Located on the north end of the building the electrical cabinet. | 2027
83470 |  | (CN) JLL-110 Cottage 500-514 (JL-13 M.U. (8)) | DM | Replenish missing roof gravel over unit 504 west side. 2% of roof gravel. Tar & Gravel, Roof Finish with 4" metal drip edge Located at entire roof. | 2027
83470 |  | (CN) JLL-110 Cottage 500-514 (JL-13 M.U. (8)) | LMAC | Adjust the threshold rise at both units 504 and 506 so that threshold and floor level changes a maximum of 1/2" at accessible doors and beveled with a slope no greater than 1:2 as per code ADAABAG Section 404.2.5, 36" x 80" Wood, Exterior Entrance Door, Deadbolt and Door Handle, Painted Located at west wall entries to units 504 and 506. | 2027
83470 |  | (CN) JLL-110 Cottage 500-514 (JL-13 M.U. (8)) | LMAC | Add horizontal grab bar at the foot of the tub (by the controls) that is at least 42" long for stabilization while a person with a disability adjusts the water controls as per code Department of Justice, ADAABAG 607.4.1.2 located in 506. | 2027
83470 |  | (CN) JLL-110 Cottage 500-514 (JL-13 M.U. (8)) | LMAC | Replace horizontal grab bars at the foot of the tub (by the controls) that is at least 24" long for stabilization while a person with a disability adjusts the water controls as per code Department of Justice, ADAABAG 607.4.1.2, Located in the bathroom of the guestroom 504 and 506 | 2027
83470 |  | (CN) JLL-110 Cottage 500-514 (JL-13 M.U. (8)) | LMAC | Replace tub diverters so that the faucet controls and shower diverter be turned on and off easily and are they operable and usable with one hand, without tight grasping, pinching, or twisting of the wrist as per code Department of Justice, ADAABAG 309.4, 8" diameter Metal, Mixing Valve - Tub/Shower Located at the tubs in units 504 and 506. | 2027
83470 |  | (CN) JLL-110 Cottage 500-514 (JL-13 M.U. (8)) | LMAC | Add pipe insulations so that lavatory in each accessible guestroom bathrooms have drain and hot water pipes that are insulated or otherwise configured to protect against contact as per code Department of Justice, ADAABAG 15" x 12" Porcelain, Lavatory, under mounted located in the bathroom of units 504 and 506. | 2027
83470 |  | (CN) JLL-110 Cottage 500-514 (JL-13 M.U. (8)) | LMAC | Adjust the thermostat height so that the HVAC controls in accessible guestrooms 504 & 506 are placed a maximum of 48” to the highest operating mechanism if the reach is unobstructed as per code ADAABAG Section 308.2.1 308.2.2, Located in both ADA rooms 504 and 506. | 2027
83470 |  | (CN) JLL-110 Cottage 500-514 (JL-13 M.U. (8)) | LMCO | Install a GFCI protected outlet to enhance electrical safety around water sources as per code 210.8(A) Dwelling units. Grounded, Standard 3-Wire Receptacle, Located in the bathrooms of each unit. | 2027
83471 |  | (CN) JLL-111 Cottage 516-530 (JL-14 M.U. (8)) | DM | Repair damaged members at canopies located at 522, 524, & 526 68" x 93" Rafters - Wood, Canopy Construction Sunshade, Painted, Constructed with 2" x 8" frame sides and twelve 1" x 8" slats. Slats are 64" long each. 1" x 4" strip 93" long is located at the center. With 3/4" bolt hardware at either side as hinge. Located on east elevation. | 2027
83471 |  | (CN) JLL-111 Cottage 516-530 (JL-14 M.U. (8)) | LMCO | Label Electrical panel per NEC Code Reference 110.22 20" x 40" Metal Panel Box, Main Electrical Service Panel, Square D brand, with 32 Breakers, 150 Amp/3 Wire System Located on exterior of the south end of the building. | 2027
83471 |  | (CN) JLL-111 Cottage 516-530 (JL-14 M.U. (8)) | LMCO | Provide knock-out cover for missing slot on electrical panel as per the NEC Code Reference 408.7 & 110.12(A); 20" x 40" Metal Panel Box, Main Electrical Service Panel, Square D brand, with 32 Breakers, 150 Amp/3 Wire System located on exterior of the south end of the building. | 2027
83472 |  | (CN) JLL-112 Cottage 532 - 544 (JL-15 M.U. (7)) | DM | Replace missing gravel on roof (approximately 5%) Tar & Gravel, Roof Finish with 4" metal drip edge Located at entire roof. (124 LF) | 2027
83473 |  | (CN) JLL-113 Cottage 546 - 552 (JL-16 M.U. (4)) | DM | Repair foundation as it is spalled severely. Concrete, Thickened Edge Slab on Grade, 4" Thick, Reinforced. | 2027
83473 |  | (CN) JLL-113 Cottage 546 - 552 (JL-16 M.U. (4)) | DM | Replenish missing gravel at southwestern edge of roof. Approximately 5% of roof. Tar & Gravel, Roof Finish with 6" metal drip edge located at entire roof. | 2027
83473 |  | (CN) JLL-113 Cottage 546 - 552 (JL-16 M.U. (4)) | DM | Repair roof flashing as roof is delaminating providing a leak risk. Tar & Gravel, Roof Finish with 6" metal drip edge located at entire roof. | 2027
83474 |  | (CN) JLL-117 Cottage 350 - 365 (JL-17 M.U. (16)) | CRDM | Replace utility vault located at Northeast corner of structure as it is past end of useful life. | 2027
83474 |  | (CN) JLL-117 Cottage 350 - 365 (JL-17 M.U. (16)) | DM | Repair damaged roof corner as decking is rotted out at Front porch of unit 361. | 2027
83474 |  | (CN) JLL-117 Cottage 350 - 365 (JL-17 M.U. (16)) | LMAC | Adjust the rise of the threshold that is approximately 2" so that the floor level changes a maximum of 1/2" at accessible doors and has a beveled a slope no greater than 1:2. as per ADAABAG Section 404.2.5; 35" x 79" Metal, Exterior Entrance Door, Deadbolt and Door Handle, Painted Located at accessible suite No. 358 | 2027
83474 |  | (CN) JLL-117 Cottage 350 - 365 (JL-17 M.U. (16)) | LMAC | Replace handle hardware with handle that has a shape that is easy to grasp with one hand and not require tight grasping, tight pinching or twisting of the wrist to operate; as per ADAABAG Section 309.4; located at front entry to suite 358. | 2027
83474 |  | (CN) JLL-117 Cottage 350 - 365 (JL-17 M.U. (16)) | LMAC | Replace the grab bar so that the toilet in each accessible guestroom bathroom have a horizontal grab bar along the adjacent side wall that is at least 42" long and mounted 33"-36" above the floor for stabilization and assistance as per code Department of Justice, ADAABAG 604.5.1, 36" Stainless Steel, Grab Bar Located on the wall adjacent the toilet in the bathroom of unit 358 | 2027
83474 |  | (CN) JLL-117 Cottage 350 - 365 (JL-17 M.U. (16)) | LMAC | Replace the grab bar that is 24" long so that the accessible toilet in each accessible guestroom bathroom have a horizontal grab bar along the wall behind the toilet that is at least 36" long and mounted 33"-36" above the floor for stabilization and assistance as per code Department of Justice, ADAABAG 604.5.2, Located behind the toilet in the bathroom of unit 358. | 2027
83474 |  | (CN) JLL-117 Cottage 350 - 365 (JL-17 M.U. (16)) | LMAC | Add a horizontal grab bar at the foot of the tub (by the controls) that is at least 24" long for stabilization while a person with a disability adjusts the water controls. [See Figure 607.4.1.2] as per code Department of Justice, ADAABAG 607.4.1.2, Grab Bar Located in the bathroom of unit 358 | 2027
83474 |  | (CN) JLL-117 Cottage 350 - 365 (JL-17 M.U. (16)) | LMAC | Add a horizontal grab bar at the head of the tub that is at least 12" long for stabilization and aid in transfer from a wheelchair to the fixed tub seat as per code Department of Justice, ADAABAG 607.4.2.3, Grab Bar Located in shower in the bathroom of unit 358 | 2027
83474 |  | (CN) JLL-117 Cottage 350 - 365 (JL-17 M.U. (16)) | LMAC | Add horizontal grab bars on the side wall of the tub so there are two grab bars (One high and One low) that are at least 24" long, per Department of Justice, ADAABAG 607.4.2.1; located in the bathroom of cottage 358 | 2027
83474 |  | (CN) JLL-117 Cottage 350 - 365 (JL-17 M.U. (16)) | LMAC | Adjust the height of the closet rod so that the rod and shelf in the clothes closet or wall mounted unit between 40" and 48 as per code Department of Justice, ADAABAG, 48" x 84" x 34" Wood, Closet - Built Out Painted cabinet, one side with mirrored door (19x80) and 4 shelves @ 25" wide and 8" deep, on the other side 4 shelves @ 19" wide and 8" deep. Located in room 358. | 2027
83474 |  | (CN) JLL-117 Cottage 350 - 365 (JL-17 M.U. (16)) | LMAC | Install protective wraps for water and drain lines so they are configured to protect against contact as per ADAABAG Section 606.5 located in the ADA bathroom of cottage 358. | 2027
83474 |  | (CN) JLL-117 Cottage 350 - 365 (JL-17 M.U. (16)) | LMCO | Investigate why all are wired with an open ground. Investigate if they need rewiring for the wires to the outlets are only two wires they should be replaced with outlets that have a ground. Grounded, Standard 3-Wire Receptacle, Located throughout the building. | 2027
83474 |  | (CN) JLL-117 Cottage 350 - 365 (JL-17 M.U. (16)) | LMCO | Replace outlets in all bathrooms to GFCI outlets per code 210.8(A), Grounded, Standard 3-Wire Receptacle. | 2027
83474 |  | (CN) JLL-117 Cottage 350 - 365 (JL-17 M.U. (16)) | LMCO | Investigate as to why the GFCI’s have an open ground; Push Reset, GFCI Protected Receptacle, Located in the bedrooms to the right of the bedroom sink. | 2027
83474 |  | (CN) JLL-117 Cottage 350 - 365 (JL-17 M.U. (16)) | RMDM | Repaint beams located at structure for decks as finish is beyond end of useful life. 3" x 6" Wood, Beam Painted. With steel plates. Located running length of south side of structure beneath second-story decks with V-shaped cross bracing beneath each individual deck. (436 LF) | 2027
83475 |  | (CN) JLL-116 Cottage 560 - 579 (JL-18 M.U. (20)) | LMAC | Adjust the threshold and floor level changes a maximum of 1/2" at accessible doors and beveled with a slope no greater than 1:2 as per code ADAABAG Section 404.2.5 32" x 80" Wood, Exterior Entrance Door, Deadbolt and Door Handle, Painted Solid core. Located at entry to units 572 and 574. | 2027
83475 |  | (CN) JLL-116 Cottage 560 - 579 (JL-18 M.U. (20)) | LMAC | Adjust the height of the closet rod so that the rod and shelf in the clothes closet or wall mounted unit between 40" and 48" as per code Department of Justice, ADAABAG, 28" x 84" x 9" Wood, Closet - Built Out With built-in shelves. Located in accessible units 572 and 574 | 2027
83475 |  | (CN) JLL-116 Cottage 560 - 579 (JL-18 M.U. (20)) | LMAC | Replace grab bar so that the toilet in each accessible guestroom bathroom have a horizontal grab bar along the adjacent side wall that is at least 42" long and mounted 33"-36" above the floor for stabilization and assistance as per code Department of Justice, ADAABAG 604.5.1, 1.5" diameter x 36" Stainless Steel, Grab Bar Located in the bathroom of accessible units 572 and 574. | 2028
83475 |  | (CN) JLL-116 Cottage 560 - 579 (JL-18 M.U. (20)) | LMAC | Replace grab bar so that the toilet in each accessible guestroom bathroom have a horizontal grab bar along the wall behind the toilet that is at least 36" long and mounted 33"-36" above the floor for stabilization and assistance as per code Department of Justice, ADAABAG 604.5.2, 1.5" diameter x 24" Stainless Steel, Grab Bar Located in the bathroom of accessible units 572 and 574. | 2028
83475 |  | (CN) JLL-116 Cottage 560 - 579 (JL-18 M.U. (20)) | LMAC | Add pipe insulate so that the lavatory in each accessible guestroom bathroom have drain and hot water pipes that are insulated or otherwise configured to protect against contact as per code Department of Justice, ADAABAG, located in the bathroom of guestroom 572 | 2028
83475 |  | (CN) JLL-116 Cottage 560 - 579 (JL-18 M.U. (20)) | LMAC | Replace tub diverter so that it can be turned on and off easily and are operable and usable with one hand, without tight grasping, pinching, or twisting of the wrist as per code Department of Justice, ADAABAG 309.4, Located in bathroom of guestroom 572 | 2028
83475 |  | (CN) JLL-116 Cottage 560 - 579 (JL-18 M.U. (20)) | LMCO | Replace GFCI outlet in unit 562, 560 as outlet does not trip when tested as per code 210.8(A) Dwelling units, Push Reset, GFCI Protected Receptacle. | 2028
83475 |  | (CN) JLL-116 Cottage 560 - 579 (JL-18 M.U. (20)) | LMLS | Repair the floor outlet mounting for the floor outlet in unit 579. Grounded, Standard 3-Wire Receptacle Floor outlet. | 2028
83476 |  | (CN) JLL-115 Cottage 900 - 912 (JL-19 M.U. (13)) | CRDM | Replace as it is beyond its useful life; 84" x 174" Wood, Exterior deck, 2x6 decking with 2x6 furring. Located beside room 912 on West side. | 2028
83476 |  | (CN) JLL-115 Cottage 900 - 912 (JL-19 M.U. (13)) | DM | Repair severe spalling at west end of structure. Concrete, Thickened Edge Slab on Grade, 4" Thick, Reinforced with 16-inch apron and 36-inch-deep grade beam. | 2028
83476 |  | (CN) JLL-115 Cottage 900 - 912 (JL-19 M.U. (13)) | DM | Repair hole in rear mechanical room wall to prevent rodent entry.1" x 9" Wood, Exterior Siding Material, Painted Vertical. | 2028
83476 |  | (CN) JLL-115 Cottage 900 - 912 (JL-19 M.U. (13)) | DM | Repair broken entry door room 906. 36" x 80" Wood, Exterior Entrance Door, Deadbolt and Door Handle, Painted | 2028
83476 |  | (CN) JLL-115 Cottage 900 - 912 (JL-19 M.U. (13)) | DM | Repair door frame at second-story utility room door; 36" x 80" Wood, Exterior Entrance Door, Deadbolt and Door Handle, Painted | 2028
83476 |  | (CN) JLL-115 Cottage 900 - 912 (JL-19 M.U. (13)) | LMAC | Adjust the threshold so that it changes a maximum of 1/2" at accessible doors and beveled with a slope no greater than 1:2 as per ADAABAG Section 404.2.5; Located at entry to unit 906. | 2028
83476 |  | (CN) JLL-115 Cottage 900 - 912 (JL-19 M.U. (13)) | LMAC | Replace the grab bar in the accessible guestroom bathroom to have a horizontal grab bar along the adjacent side wall that is at least 42" long and mounted 33"-36" above the floor for stabilization and assistance as per code Department of Justice, ADAABAG 604.5.1, 36" Stainless Steel Grab Bar Located in ADA bathroom in room 906 on wall adjacent to the toilet. | 2028
83476 |  | (CN) JLL-115 Cottage 900 - 912 (JL-19 M.U. (13)) | LMAC | Add a horizontal grab bar at the head of the tub that is at least 12" long for stabilization and aid in transfer from a wheelchair to the fixed tub seat as per code Department of Justice, ADAABAG 607.4.2.3, Located in ADA bathroom at the tub on the back wall in room 906. | 2028
83476 |  | (CN) JLL-115 Cottage 900 - 912 (JL-19 M.U. (13)) | LMAC | Add pipe insulation to drain and hot water pipes per, Department of Justice, ADAABAG; located in the bathroom of cottage 906 | 2028
83476 |  | (CN) JLL-115 Cottage 900 - 912 (JL-19 M.U. (13)) | LMAC | Replace toilet with so that the seat in each accessible toilet is between 17"-19" above the floor as per Department of Justice, ADAABAG, located in the ADA bathroom of room 906 | 2028
83476 |  | (CN) JLL-115 Cottage 900 - 912 (JL-19 M.U. (13)) | LMFS | Replace Walls of mechanical room as they need to be fire rated, Gypsum Board, Interior Wall Covering Material, Factory Finish Located on all walls throughout each room throughout building. | 2028
83476 |  | (CN) JLL-115 Cottage 900 - 912 (JL-19 M.U. (13)) | LMFS | Add fire rated sheetrock to Ceiling in mechanical room; Gypsum Board, Interior Ceiling Covering Material, Painted Located in all lower-level guestrooms, and upper-level guestroom bathrooms. | 2028
83477 |  | (CN) JLL-114 Cottage 700 - 719 (JL-20 M.U. (20)) | DM | Inspect beams by a structural engineer to confirm that they are structurally sound and rated for the concrete decks they hold up; 2" x 8" Wood Beam, Balcony Framing Wood ledger bolted to the rear of the building for support of the wood deck, Painted. Continuous along the rear of the building (957 SF). | 2028
83477 |  | (CN) JLL-114 Cottage 700 - 719 (JL-20 M.U. (20)) | DM | Repair Siding especially on the south side of the building where it is warped; Wood, Exterior Siding Material, painted 4" horizontal rough sawn wood siding, painted. Located around the entire building exterior. | 2028
83477 |  | (CN) JLL-114 Cottage 700 - 719 (JL-20 M.U. (20)) | DM | Repair cracked & damaged drywall at kitchenette at corner wall in units; 704, 706, 710, & 718 Gypsum Board, Interior Wall Covering Material. | 2028
83478 |  | (CN) JLL-118 Cottage 201 - 211 (JL-21 M.U. (6)) | DM | repair rotted wood in outside corner where low roof intersects, 2" X 6", Wood Framing, Exterior Wall Frame Assembly, @ 16" O. C., with plywood sheeting and rolled insulation Located throughout exterior of building. (302 LF) | 2028
83478 |  | (CN) JLL-118 Cottage 201 - 211 (JL-21 M.U. (6)) | DM | Repair drip edge above room 207, Tar & Gravel, Roof Finish, with 6" metal drip edge, located throughout roof Including entry canopies | 2028
83478 |  | (CN) JLL-118 Cottage 201 - 211 (JL-21 M.U. (6)) | DM | replace rotting wood and repaint where rainwater runoff has damaged low roof edge, 2" X 6", Wood, Fascia Board, Painted, Located at perimeter of roof | 2028
83478 |  | (CN) JLL-118 Cottage 201 - 211 (JL-21 M.U. (6)) | DM | Secure the toilet seat located in the bathroom of unit 205 is not properly secured. | 2028
83478 |  | (CN) JLL-118 Cottage 201 - 211 (JL-21 M.U. (6)) | LMCO | Install conduit at electrical panel as per code NEC Article 334.15, 12" x 30" Metal Panel Box, Main Service Panel, Square D brand, with, 20 Breakers, 150 Amp/3 Wire System With main service disconnect. At 150 amp. Located in the northwest corner of the building | 2028
83479 |  | (CN) JLL-119 Cottage 200 - 214 & 401-415 (JL-22 M.U. (16)) | DM | Replace missing gravel approximately (3%) over the entire roof; Tar & Gravel, Roof Finish, with 6" metal drip edge Located at entire roof. | 2028
83479 |  | (CN) JLL-119 Cottage 200 - 214 & 401-415 (JL-22 M.U. (16)) | LMAC | Adjust threshold so the floor level changes are a maximum of 1/2" and with a beveled slope no greater than 1:2; as per ADAABAG Section 404.2.5; 34" x 78" Metal, Exterior Entrance Door, Deadbolt and Door Handle, Painted Located at unit entries 202, 210 and 208. | 2028
83479 |  | (CN) JLL-119 Cottage 200 - 214 & 401-415 (JL-22 M.U. (16)) | LMAC | Adjust threshold so the floor level changes are a maximum of 1/2" and with a beveled slope no greater than 1:2; as per ADAABAG Section 404.2.5; 36" x 80" Wood, Exterior Entrance Door, Deadbolt and Door Handle, Painted solid core. Located at units 401, and 403. | 2028
83479 |  | (CN) JLL-119 Cottage 200 - 214 & 401-415 (JL-22 M.U. (16)) | LMAC | Adjust height of the rod in Accessible Guest Rooms and Suites-Closet Rod/Shelf mounted between 40" and 48 as per Department of Justice, ADAABAG located in unit 202, 208, 210, 401, & 403. | 2028
83479 |  | (CN) JLL-119 Cottage 200 - 214 & 401-415 (JL-22 M.U. (16)) | LMAC | Replace tub/shower diverter with one that can be turned on and off easily and can be operated and useable with one hand, without tight grasping, pinching, or twisting of the wrist; per Department of Justice, ADAABAG 309.4, located in bathroom of cottages 210, 401, & 403. | 2028
83479 |  | (CN) JLL-119 Cottage 200 - 214 & 401-415 (JL-22 M.U. (16)) | LMAC | Add grab bar to the opposite wall of the seat, as per Department of Justice, ADAABAG 608.3.2. in bathroom of cottage 202 & 208 | 2028
83479 |  | (CN) JLL-119 Cottage 200 - 214 & 401-415 (JL-22 M.U. (16)) | LMAC | Add drain and hot water pipe insulation protection, per Department of Justice, ADAABAG on pipes below sinks in bathrooms of cottage 210. | 2028
83479 |  | (CN) JLL-119 Cottage 200 - 214 & 401-415 (JL-22 M.U. (16)) | LMAC | Add horizontal grab bars that are 24" long at the foot of the tub, per Department of Justice, ADAABAG 607.4.1.2 in bathroom of cottages 210, 401, & 403. | 2028
83479 |  | (CN) JLL-119 Cottage 200 - 214 & 401-415 (JL-22 M.U. (16)) | LMAC | Add horizontal grab bar that are at least 12" long at the head of the tub, per Department of Justice, ADAABAG 607.4.2.3 in bathroom of cottages 210, 401, & 403. | 2028
83479 |  | (CN) JLL-119 Cottage 200 - 214 & 401-415 (JL-22 M.U. (16)) | LMAC | Add grab bars so that there are two grab bars on the side wall of the tub (one high and one low) and are at least 24" long, per Department of Justice, ADAABAG 607.4.2.1; located in the bathrooms of cottages 210, 401, 403. | 2028
83479 |  | (CN) JLL-119 Cottage 200 - 214 & 401-415 (JL-22 M.U. (16)) | LMAC | Adjust the thermostats that are 52" above finished floor so that HVAC controls in accessible guestrooms placed a maximum of 48” to the highest operating mechanism if the reach is unobstructed as per ADAABAG Section 308.2.1 308.2.2 located in Units 202, 208, 210, 401, & 403 | 2028
83481 |  | (CN) JLL-120 Cottage 216 - 222 & 417-423 (JL-23 M.U. (8)) | DM | Replace damaged and rotted 3" x 6" joists Located at (2) locations 216 & 218. | 2028
83482 |  | (CN) JLL-121 Cottage 224 - 234 & 425-435 (JL-24 M.U. (12)) | DM | Replace missing gravel (approximately 5%) Tar & Gravel, Roof Finish with 6" metal drip edge located on entire roof | 2028
83482 |  | (CN) JLL-121 Cottage 224 - 234 & 425-435 (JL-24 M.U. (12)) | DM | Replace damaged fascia board located cottages 232 & 234 approximately 16 LF 2" x 6" Wood, Fascia Board Painted. | 2028
83482 |  | (CN) JLL-121 Cottage 224 - 234 & 425-435 (JL-24 M.U. (12)) | DM | Replace water damaged drywall in cottages 232 & 429 Gypsum Board, Interior Ceiling Covering Material, Painted. | 2028
83482 |  | (CN) JLL-121 Cottage 224 - 234 & 425-435 (JL-24 M.U. (12)) | DM | Investigate nasty smell in cottage 433, 4" diameter Plastic - ABS, Waste & Vent Piping Main waste line and roof stack penetrations. | 2028
83483 |  | (CN) JLL-122 Cottage 236-246, 437-44 (JL-25 M.U. (12)) | DM | Replace missing gravel (approximately 3%) Tar & Gravel, Roof Finish, with 6" metal drip edge Located at entire roof | 2028
83484 |  | (CN) JLL-123 Cottage 400 - 418 & 601-619 (JL-26 M.U. (20)) | DM | Repair damage foundation wall located at Room 400, 617, 24" X 12", Concrete, Continuous Footing, Located at perimeter of building and between units. | 2028
83484 |  | (CN) JLL-123 Cottage 400 - 418 & 601-619 (JL-26 M.U. (20)) | DM | Repair and or replace damaged and broken shingle siding, 5%, 24" X 12", Exterior Siding Material, Lap, Painted, Asbestos lab shingle mailed to exterior, Located throughout exterior of building | 2028
83484 |  | (CN) JLL-123 Cottage 400 - 418 & 601-619 (JL-26 M.U. (20)) | DM | Repair flashing at roof and wall connection to prevent water damage, Tar & Gravel, Roof Finish, with 6" metal drip edge. | 2028
83484 |  | (CN) JLL-123 Cottage 400 - 418 & 601-619 (JL-26 M.U. (20)) | DM | Replace missing gravel on tar and gravel roof 10%, Tar & Gravel, Roof Finish, with 6" metal drip edge, located throughout roof Including entry canopies | 2028
83484 |  | (CN) JLL-123 Cottage 400 - 418 & 601-619 (JL-26 M.U. (20)) | LMAC | Adjust the threshold so that threshold and floor level changes a maximum of 1/2" at accessible doors and beveled with a slope no greater than 1:2 as per code ADAABAG Section 404.2.5 located at door to unit 402. | 2028
83484 |  | (CN) JLL-123 Cottage 400 - 418 & 601-619 (JL-26 M.U. (20)) | LMAC | Add horizontal grab bar at the foot of the tub (by the controls) that is at least 24" long for stabilization while a person with a disability adjusts the water controls as per code Department of Justice, ADAABAG 607.4.1.2, Located in the bathroom of the guestroom of 402. | 2028
83484 |  | (CN) JLL-123 Cottage 400 - 418 & 601-619 (JL-26 M.U. (20)) | LMAC | Add horizontal grab bar at the head of the tub that is at least 12" long for stabilization and aid in transfer from a wheelchair to the fixed tub seat as per code Department of Justice, ADAABAG 607.4.2.3, Located bathroom of the guestroom 402 | 2028
83484 |  | (CN) JLL-123 Cottage 400 - 418 & 601-619 (JL-26 M.U. (20)) | LMAC | Add horizontal grab bars on the side wall of the tub so there are two grab bars (One high and One low) that are at least 24" long, per Department of Justice, ADAABAG 607.4.2.1; located in the bathroom of cottage 402. | 2028
83484 |  | (CN) JLL-123 Cottage 400 - 418 & 601-619 (JL-26 M.U. (20)) | LMAC | Replace grab bar so that the toilet in each accessible guestroom bathroom have a horizontal grab bar along the adjacent side wall that is at least 42" long and mounted 33"-36" above the floor for stabilization and assistance as per code Department of Justice, ADAABAG 604.5.1, 1.5" diameter x 36" Stainless Steel Grab Bar located adjacent to the toilet in the bathroom of the guestroom 402 | 2028
83484 |  | (CN) JLL-123 Cottage 400 - 418 & 601-619 (JL-26 M.U. (20)) | LMAC | Replace grab bar so that the toilet in each accessible guestroom bathroom have a horizontal grab bar along the wall behind the toilet that is at least 36" long and mounted 33"-36" above the floor for stabilization and assistance as per code Department of Justice, ADAABAG 604.5.2, 1.5" diameter x 24" Stainless Steel Grab Bar located behind toilet in the bathroom of the guestroom 402 | 2028
83484 |  | (CN) JLL-123 Cottage 400 - 418 & 601-619 (JL-26 M.U. (20)) | LMAC | Add pipe insulation so that the lavatory in each accessible guestroom bathroom have drain and hot water pipes that are insulated or otherwise configured to protect against contact as per code Department of Justice, ADAABAG, Located in the bathroom of guestroom 402 | 2028
83484 |  | (CN) JLL-123 Cottage 400 - 418 & 601-619 (JL-26 M.U. (20)) | LMAC | Replace tub/shower diverter with one that can be turned on and off easily and can be operated and useable with one hand, without tight grasping, pinching, or twisting of the wrist; per Department of Justice, ADAABAG 309.4, located in bathroom of cottage 402. | 2028
83484 |  | (CN) JLL-123 Cottage 400 - 418 & 601-619 (JL-26 M.U. (20)) | LMAC | Adjust the thermostat so that the HVAC controls in accessible guestroom 402 are placed a maximum of 48” to the highest operating mechanism if the reach is unobstructed as per code ADAABAG Section 308.2.1 308.2.2, located in room 402. | 2028
83484 |  | (CN) JLL-123 Cottage 400 - 418 & 601-619 (JL-26 M.U. (20)) | LMCO | Install sufficient labeling as per code 110.22 12" x 30" Metal Panel Box, Electrical Sub Panel, Square D brand, with 30 Breakers, 200 Amp/3 Wire System Has a single breaker disconnect of 200 amp. Located along the east wall in the mechanical room/ice room. | 2028
83484 |  | (CN) JLL-123 Cottage 400 - 418 & 601-619 (JL-26 M.U. (20)) | LMCO | Label the electrical panel as per code 110.22, 14" x 34" Metal Panel Box, Electrical Sub Panel Trumbull electric. 30 breaker 210 amp. Located on the unit bump out along the north wall near unit 408. | 2028
83485 |  | (CN) JLL-124 Cottage 420 - 426 & 621-627 (JL-27 M.U. (8)) | DM | Repair spalling concrete on foundation wall south end of room 420, 621, 623 (45 LF). | 2028
83485 |  | (CN) JLL-124 Cottage 420 - 426 & 621-627 (JL-27 M.U. (8)) | DM | Repair roof flashing at intersection of wall in lower roof to prevent water damage of siding and wall, Tar & Gravel, Roof Finish, with 6" metal drip edge, located throughout roof Including entry canopies | 2028
83485 |  | (CN) JLL-124 Cottage 420 - 426 & 621-627 (JL-27 M.U. (8)) | RMDM | Repaint fascia board as it is past due; 2" x 6" Wood, Fascia Board Painted. Located at perimeter of roof. (336 LF) | 2028
83486 |  | (CN) JLL-125 Cottage 428 - 446 & 629-647 (JL-28 M.U. (20)) | DM | Replace damaged and spalling stoops at units 428/430 39" x 53" Concrete, Entrance Stoop - Pad 4”. Located in front of rooms 428/430, | 2028
83487 |  | (CN) JLL-126 Cottage 600 - 610 & 801-811 (JL-29 M.U. (12)) | DM | Replace rotted wall members located between units 602 and 604 as wall is hanging precariously off foundation. Damage is caused by improper roof flashing and siding interaction. | 2028
83487 |  | (CN) JLL-126 Cottage 600 - 610 & 801-811 (JL-29 M.U. (12)) | DM | Replenish missing gravel at approximately 5% of roof around obstacles and roof edges. Tar & Gravel, Roof Finish with 6" metal drip edge Located at entire roof. | 2028
83487 |  | (CN) JLL-126 Cottage 600 - 610 & 801-811 (JL-29 M.U. (12)) | LMAC | Adjust the threshold so that threshold and floor level changes a maximum of 1/2" at accessible doors and beveled with a slope no greater than 1:2 as per code ADAABAG Section 404.2.5, 34" x 78" Metal, Exterior Entrance Door, Deadbolt and Door Handle, painted located at both units 803 and 805. | 2028
83487 |  | (CN) JLL-126 Cottage 600 - 610 & 801-811 (JL-29 M.U. (12)) | LMAC | Replace grab bar so that the toilet in each accessible guestroom bathroom have a horizontal grab bar along the adjacent side wall that is at least 42" long and mounted 33"-36" above the floor for stabilization and assistance as per code Department of Justice, ADAABAG 604.5.1, 36" Stainless Steel, Grab Bar Located in room 805, 803 | 2028
83487 |  | (CN) JLL-126 Cottage 600 - 610 & 801-811 (JL-29 M.U. (12)) | LMAC | Replace the grab bars so the accessible toilet in each accessible guestroom bathroom has a horizontal grab bar along the wall behind the toilet that is at least 36" long and mounted 33"-36" above the floor for stabilization and assistance as per code Department of Justice, ADAABAG 604.5.2, 24" Stainless Steel, Grab Bar Located in the bathroom of guestrooms 803 and 805 | 2028
83487 |  | (CN) JLL-126 Cottage 600 - 610 & 801-811 (JL-29 M.U. (12)) | LMAC | Install a horizontal grab bar at the head of the tub that is at least 12" long for stabilization and aid in transfer from a wheelchair to the fixed tub seat as per code Department of Justice, ADAABAG 607.4.2.3, Located in the bathroom of guestrooms 803 and 805 | 2028
83487 |  | (CN) JLL-126 Cottage 600 - 610 & 801-811 (JL-29 M.U. (12)) | LMAC | Install a horizontal grab bar at the foot of the tub (by the controls) that is at least 24" long for stabilization while a person with a disability adjusts the water controls as per code Department of Justice, ADAABAG 607.4.1.2, Located in the bathroom of guestrooms 803 and 805 | 2028
83487 |  | (CN) JLL-126 Cottage 600 - 610 & 801-811 (JL-29 M.U. (12)) | LMAC | Add grab bars so that there are two grab bars on the side wall of the tub (one high and one low) and are at least 24" long, per Department of Justice, ADAABAG 607.4.2.1; located in the bathrooms of cottages 803 & 805. | 2028
83487 |  | (CN) JLL-126 Cottage 600 - 610 & 801-811 (JL-29 M.U. (12)) | LMAC | Add pipe protection on the drain and hot water pipes per, Department of Justice, ADAABAG located in the bathrooms of cottages 803 & 805. | 2028
83488 |  | (CN) JLL-127 Cottage 612 - 618 & 813-819 (JL-30 M.U. (8)) | DM | Repair spalling foundation wall. 8" X 48", Concrete, Foundation Wall, Located at perimeter of building and between units. | 2028
83488 |  | (CN) JLL-127 Cottage 612 - 618 & 813-819 (JL-30 M.U. (8)) | DM | Replace rotting wood in 2 x 4 wall at outside corner where in the roof meets exterior wall on east and west elevations | 2028
83488 |  | (CN) JLL-127 Cottage 612 - 618 & 813-819 (JL-30 M.U. (8)) | DM | Replace flashing at low roof where intersects with wall on east and west elevations to prevent water damage to wall below, Tar & Gravel, Roof Finish, with 6" metal drip edge, located above entire roof including at entry canopies | 2028
83488 |  | (CN) JLL-127 Cottage 612 - 618 & 813-819 (JL-30 M.U. (8)) | DM | Repaint drip edge behind sunshade canopies, Tar & Gravel, Roof Finish, with 6" metal drip edge, Located along low edge of roof slope at east and west elevations. (107 Total LF) | 2028
83488 |  | (CN) JLL-127 Cottage 612 - 618 & 813-819 (JL-30 M.U. (8)) | DM | Replace rotten fascia board at low slope of roof on East and West elevations, 2" X 6", Wood, Fascia Board, Painted. (107 Total LF) | 2028
83488 |  | (CN) JLL-127 Cottage 612 - 618 & 813-819 (JL-30 M.U. (8)) | DM | Replace damaged or missing caulk around the tubs where tile meets the tub.8" x 8" Tile - Ceramic, Interior Wall Covering Material With ceramic wall mounted soap dish. Located around tub/shower in bathrooms throughout. | 2028
83488 |  | (CN) JLL-127 Cottage 612 - 618 & 813-819 (JL-30 M.U. (8)) | DM | Replace damaged utility vault cover; 2 x 6 decking covering vault. Located at interior on north side of linen room. | 2028
83488 |  | (CN) JLL-127 Cottage 612 - 618 & 813-819 (JL-30 M.U. (8)) | LMCO | Install new GFCI outlet as per code 210.8(A) Dwelling units, Grounded, Standard 3-Wire Receptacle Located in the mechanical pit. | 2028
83491 |  | (CN) JLL-005 Cabana/Pool (JL-32 Cabana/Pool) | CRDM | Replace damage swamp cooler as it has been crushed by roof. 36" x 36" Self-Contained, Enclosed, Roof Top Package Unit, Swamp cooler with 24" x 24“ ducting approximately three LF. Located on interior roof. | 2028
83491 |  | (CN) JLL-005 Cabana/Pool (JL-32 Cabana/Pool) | DM | Repair broken Plexiglas sheets at roof finish (26 SF) | 2028
83491 |  | (CN) JLL-005 Cabana/Pool (JL-32 Cabana/Pool) | LMCO | Install Seismic Strapping as per UPC (Uniformed Plumbing Code) Reference 507.2; Gas Fired, Water Heater - Residential, Rheem, 40 Gallon, with 10 diameter flue venting Prog40-36p rh62. Located in sales room. | 2028
83492 |  | (CN) JLL-006 Stable/Corral Bldg (HS) JL-22 Jackson Lk Stable | DM | Replace missing door between office and hallway. 24" x 80" Hollow Core - Wood, Standard Interior Door, Lockset Hardware, Stained | 2028
83493 |  | (CN) JLL-002 Service Station ((HS) JL-018) | DM | Repair window Northwest corner of building | 2028
83493 |  | (CN) JLL-002 Service Station ((HS) JL-018) | DM | Replace missing panes in northwest and southwest windows | 2028
83493 |  | (CN) JLL-002 Service Station ((HS) JL-018) | LMLS | Replace Non-Working Emergency Lighting. 10" x 12" Wall Mounted, Emergency Exit Sign, with dual emergency lights Located above the door that accesses the bay area and oil storage room. | 2028
83494 |  | (CN) JLL-301 Staff 1 & 3 (JL-35 Staff Housing Duplex) | LMCO | Replace glass with obscuring tempered glass. 24" x 38" Wood, Glazed Window, Double Hung, Double Pane, Painted, with wood screen two panels in each window, | 2028
83495 |  | (CN) JLL-302 Staff 5 & 7 (JL-36 Staff Housing Dupl | DM | Repair leaking roof over south bedroom of unit S-7. Near center of building west side. | 2028
83496 |  | (CN) JLL-303 Staff 9&11,15-1,15-2,15-3,15-4,15A&B (JL-37) | CRDM | Replace as it is past it's useful life; 34" x 80" Wood, with Self-Closing Device, Lockset with Key, Painted, Exterior Entrance Door with 24“ x 30“ three panel true divided vision lite located at west exterior wall of laundry hallway. | 2028
83496 |  | (CN) JLL-303 Staff 9&11,15-1,15-2,15-3,15-4,15A&B (JL-37) | CRDM | Replace as it is past it's useful life; 36" x 80" Wood, Deadbolt and Door Handle, Painted, Exterior Entrance Door, Hollow. Located on the shed door. | 2028
83496 |  | (CN) JLL-303 Staff 9&11,15-1,15-2,15-3,15-4,15A&B (JL-37) | CRDM | Replace at end of useful life; 5-Blade, without lighting, Ceiling Fan, Located in the kitchen of unit 15–1, 15-3. | 2028
83496 |  | (CN) JLL-303 Staff 9&11,15-1,15-2,15-3,15-4,15A&B (JL-37) | DM | Repair water damage at West Eveline above unit S-11. Approximately 28 ft.²; 3" x 10" Rafters - Wood, Pitched Roof Construction, @ 24 O.C., with tongue & groove roof decking Rafters are heavy timber running east to west. Decking members are 3“ x 6“ tongue and groove. Structure includes 3“ x 10“ blocking only above center bearing wall and exterior bearing walls of building between every joist. 3 x 10 intermediate blocking is included mid span of rafters | 2028
83496 |  | (CN) JLL-303 Staff 9&11,15-1,15-2,15-3,15-4,15A&B (JL-37) | DM | Replace broken window 34" X 36", Aluminum, Glazed Window, Double Hung, Single Pane, Located in East exterior screen wall around laundry room entry. (This component is part of the historic fabric and or character feature of the building.) | 2028
83496 |  | (CN) JLL-303 Staff 9&11,15-1,15-2,15-3,15-4,15A&B (JL-37) | DM | Replace damaged exterior door, storage shed in rear yard of unit S-11. 36" X 80", Wood, Exterior Entrance Door, Lockset with Key, Painted | 2028
83496 |  | (CN) JLL-303 Staff 9&11,15-1,15-2,15-3,15-4,15A&B (JL-37) | LMCO | Add Seismic strapping shall be 2” wide around the top 1/3 and the bottom 1/3 as per UPC (Uniformed Plumbing Code) Reference 507.2; Water Heater - Residential, Rheem, 50 Gallon Located in the laundry room unit 15AB. | 2028
83496 |  | (CN) JLL-303 Staff 9&11,15-1,15-2,15-3,15-4,15A&B (JL-37) | LMCO | Install seismic strapping on the top 1/3 and the bottom 1/3 of the water heater as per the UPC (Uniformed Plumbing Code) Reference 507.2. Electric, Water Heater - Residential, Bradford White, 50 Gallon Model number M250T6DS – 1NCWW. Located in the water heater closet of unit nine. | 2028
83496 |  | (CN) JLL-303 Staff 9&11,15-1,15-2,15-3,15-4,15A&B (JL-37) | LMCO | Replace regular outlets with GFCI outlets at the three outlets near the kitchen that are not currently GFCI protected, as per N.E.C. 210.8 (A) vi. | 2028
83496 |  | (CN) JLL-303 Staff 9&11,15-1,15-2,15-3,15-4,15A&B (JL-37) | LMCO | Replace outlets in the laundry room near the washing machines that are not GFCI protected. | 2028
83496 |  | (CN) JLL-303 Staff 9&11,15-1,15-2,15-3,15-4,15A&B (JL-37) | LMLS | Test shingle siding for asbestos, remediate as appropriate. Fiber Cement Siding, Exterior Siding Material, Lap, painted 12 x 24" shingle pattern, Extending from North pop out of unit AP to the north side of entry door #4, extending from south corner of laundry hallway pop out to the walkway out of unit S-9, then continuing around south wing of unit nine to unit nine West side pop out, then in between each pop out along west wall. | 2028
83496 |  | (CN) JLL-303 Staff 9&11,15-1,15-2,15-3,15-4,15A&B (JL-37) | LMLS | Install missing Cover Plate to Water Heater at top and bottom of Electric, Water Heater - Residential, State, 50 Gallon Model number ES652D0RT. Located in the water heater closet in the hallway of unit 11. | 2028
83496 |  | (CN) JLL-303 Staff 9&11,15-1,15-2,15-3,15-4,15A&B (JL-37) | LMLS | Repair GFCI outlet in the bathroom of unit 15AB that is not working properly and was wired incorrectly. | 2028
83497 |  | (CN) JLL-304 Staff 15 C-F (JL-38 Staff Housing 4-Plex) | CRDM | Replace as it is beyond its useful life; Grounded, Standard 3-Wire Receptacle, with weatherproof cover located in front of Unit E and on the south side exterior of unit C | 2028
83497 |  | (CN) JLL-304 Staff 15 C-F (JL-38 Staff Housing 4-Plex) | DM | Replace missing coat closet door in unit E; 24" x 80" Hollow Core - Wood, Standard Interior Door, Standard Door Handle, Stained | 2028
83497 |  | (CN) JLL-304 Staff 15 C-F (JL-38 Staff Housing 4-Plex) | DM | Replace missing door in closet next to bedroom unit C; 30" x 80" Wood, Sliding/Folding Door, Standard Door Handle, Stained Bi-fold door with pull knob | 2028
83498 |  | (CN) JLL-305 Staff 17 & 19 (JL-39 Staff Housing D | DM | Repair bottom edge of batt and board around perimeter of building. In several areas bottom edge of board has significant water damage is working with paint flaking and deteriorating. Batt and Board, Exterior Siding Material, Batt & Board, Painted Decorative 1/2" x 2" plywood batten boards set at 8 inches on center vertically around entire exterior perimeter. Exterior finish also includes a one and 1/2“ x 2“ plywood board mounted horizontally at soffit line around entire perimeter. | 2028
83498 |  | (CN) JLL-305 Staff 17 & 19 (JL-39 Staff Housing D | DM | Repair water damage over refrigerator from a previous roof leak; Drywall, Interior Ceiling Covering Material, Painted | 2028
83499 |  | (CN) JLL-306 Staff 21 & 23 (JL-40 Staff Housing Duplex) | DM | Replace missing gravel patches: Tar & Gravel with 6" x 2“ painted aluminum drip edge around entire perimeter of roof, and from edge of roof to ridge roof between kitchen and garage (48 LF total) Also included is a 1“ x 3“ drip edge around each of the ridge top vent caps (224 L.F... Total). Roofing also includes penetration boots for (3) 2-inch vent pipes, (2) 4-inch vent pipes, one aluminum dryer vent. Also flashing is provided around both chimneys (34 LF). Located Over entire roof structure | 2028
83499 |  | (CN) JLL-306 Staff 21 & 23 (JL-40 Staff Housing Duplex) | RMDM | Repaint fascia: 1" x 6" Wood, Fascia Board Double one by six fascia board around entire perimeter of roof structure, 388LF | 2028
83499 |  | (CN) JLL-306 Staff 21 & 23 (JL-40 Staff Housing Duplex) | RMDM | Repaint soffit covering: Plywood Sheeting, Soffit Covering, Painted 48 inch wide on east and west sides of the building, 28 inches out from exterior wall on north and south sides of buildings. Located around all four sides of buildings following rake of the roof. | 2028
83500 |  | (CN) JLL-307 Staff 2 & 4 (JL-41 Staff Housing Duplex) | DM | Replace or repair fascia board, Fascia board along west side of structure has severe deterioration. 2" x 12" Wood, Fascia Board Fascia board. (This component is part of the historic fabric and or character feature of the building.) | 2028
83500 |  | (CN) JLL-307 Staff 2 & 4 (JL-41 Staff Housing Duplex) | LMCO | Replace door from the garage to residence with a minimum 20 minutes rated door with auto closing device. 24" x 80" Hollow Core - Wood, Standard Interior Door, Single panel door Standard twist knob | 2028
83501 |  | (CN) JLL-308 Staff 6 & 8 (JL-42 Staff Housing Duplex) | CRDM | Replace as it is past it's useful life; 24' x 10' Concrete, Entrance Stoop - Pad, 4" deep. Patio, Located on the west exterior of unit S – 8 | 2028
83501 |  | (CN) JLL-308 Staff 6 & 8 (JL-42 Staff Housing Duplex) | DM | Replace flooring, Flooding damage on laminate floor and trim. Laminate located in laundry of unit S-8., Interior Floor Covering Material Wood color and texture. | 2028
83501 |  | (CN) JLL-308 Staff 6 & 8 (JL-42 Staff Housing Duplex) | LMLS | Test east wall, lap siding material for possible asbestos. Wall tiles meet criteria and installed date for potential asbestos contamination | 2028
83502 |  | (CN) JLL-309 Staff 10 & 12 & 14 & 16 (JL-43 Staff H 4-Plex) | LMCO | Provide clear space. (30") Electrical subpanel between units 14 and 16 on the exterior wall on the west side of building does not provide clear floor space as required. a. NEC Code Reference 110.26; 15" x 24" Metal Panel Box, Electrical Sub Panel, General Electric brand with 24 Breakers, 200 Amp/3 Wire System | 2028
83502 |  | (CN) JLL-309 Staff 10 & 12 & 14 & 16 (JL-43 Staff H 4-Plex) | LMCO | Provide 30 inch clear for space in front of electrical panel. As per NEC Code Reference 110.26; 30" x 30" Metal Panel Box, Main Electrical Service Panel, Siemens/ITE brand with 6 Breakers, 400 Amp/3 Wire System | 2028
83502 |  | (CN) JLL-309 Staff 10 & 12 & 14 & 16 (JL-43 Staff H 4-Plex) | LMLS | Test and remediate for potential asbestos in exterior siding material. Siding material fits pattern and install date for likely asbestos contamination. | 2028
83503 |  | (CN) JLL-310 Dorm 1 (JL-44 Staff Housing/Dorms) | DM | Install missing doors at dorm rooms, 7, 13, 21, & 23. 40" x 80" Hollow Core - Wood, Standard Interior Door, two panel door, stained Double doors with slats on the top portion solid on the bottom half. | 2028
83503 |  | (CN) JLL-310 Dorm 1 (JL-44 Staff Housing/Dorms) | DM | Replace missing drawer fronts on cabinets under sink in dorms 3, 7, 16, 20, and door front in dorm 15. 37" x 30" x 21" Sink Base, Cabinet, Wood, Stained Two fixed drawer covers and two 16 x 9" drawers, and (1) door. | 2028
83503 |  | (CN) JLL-310 Dorm 1 (JL-44 Staff Housing/Dorms) | DM | Replace damaged VCT tile by shower in dorms 9/10, 11/12, 19/20, and 21/22. 12" x 12" VCT. | 2028
83503 |  | (CN) JLL-310 Dorm 1 (JL-44 Staff Housing/Dorms) | DM | Repair spalled black top on the south end of building. 175 sf | 2028
83503 |  | (CN) JLL-310 Dorm 1 (JL-44 Staff Housing/Dorms) | LMCO | Install seismic straps on the top 1/3 and bottom 1/3 of the water heater as per IBC Reference Code (502.4) and UPC Reference 305.1. Electric, Rheem, 80 Gallon, Water Heater - Residential, located in the laundry room. Water heater includes shut off valves. Model number ELD80 – c. Serial number is Q331540 E. 56. | 2028
83503 |  | (CN) JLL-310 Dorm 1 (JL-44 Staff Housing/Dorms) | LMCO | Install GFCI outlets near washers, as per NEC section 210.8 (A) vii. Grounded, Standard 3-Wire Receptacle. | 2028
83504 |  | (CN) JLL-311 Dorm 3 (JL-45 Staff Housing/Dorms) | DM | Repair Damaged Siding, Repair damaged siding at entries. T-111, Exterior Siding Material Painted. | 2028
83504 |  | (CN) JLL-311 Dorm 3 (JL-45 Staff Housing/Dorms) | DM | Repair Broken Water Closet, Repair broken water closet in women's bathroom. | 2028
83504 |  | (CN) JLL-311 Dorm 3 (JL-45 Staff Housing/Dorms) | DM | Repair loose baseboard heater in Dorm 4.5" x 96" Metal, Electric baseboard Heater. | 2028
83505 |  | (CN) JLL-312 Employee Recreation Hall (Whistle Pig) (JL-46) | LMCO | Install panic hardware as the assembly occupancy is require panic hardware on exit doors; 36" x 80" Wood, Solid Core, with Kick Plate, Round Handle, Painted, Located in Game room on north and south walls. | 2028
83505 |  | (CN) JLL-312 Employee Recreation Hall (Whistle Pig) (JL-46) | LMCO | Add panic door hardware to door into lounge per IBC code. 36" x 80" Wood, Standard Interior Door, Standard Door Handle, Stained Located at the lounge area and fitness room. | 2028
83505 |  | (CN) JLL-312 Employee Recreation Hall (Whistle Pig) (JL-46) | LMLS | Replace missing 9", Triple Bulb, Exterior Light Fixture, (1) located at West vestibule of conference room, is missing leaving exposed wires. | 2028
83507 |  | (CN) JLL-313 Dorm 7 (JL-47 Staff Housing/Dorms) | DM | Repair Damaged Water Closet, Repair damaged water closet in women's restroom middle stall | 2028
83507 |  | (CN) JLL-313 Dorm 7 (JL-47 Staff Housing/Dorms) | DM | Reattach Face Plate, Reattached the face plate on baseboard heater in dorm 10 and 15 | 2028
83507 |  | (CN) JLL-313 Dorm 7 (JL-47 Staff Housing/Dorms) | LMCO | Label Panel and Provide Locking Cover per NEC 110.22 and reference code 408.38; 16" x 44" Metal Panel Box, Main Electrical Service Panel, 30 Breakers, 125 Amp/3 Wire System Trumbull electric. | 2028
83508 |  | (CN) JLL-314 Dorm 9 (JL-48 Staff Housing/Dorms) | DM | Replace missing gravel on approximately 25 SF of west side of roof; Tar & Gravel, with 2" metal drip edge. | 2028
83508 |  | (CN) JLL-314 Dorm 9 (JL-48 Staff Housing/Dorms) | DM | Rehang fallen doors and mend tracks in dorms 2, 4, 6, 8, 10, 3, 9, 7, 13, 17. 48" x 80" Hollow Core - Wood, Sliding/Folding Door, Standard Door Handle double Bi-fold doors (knotty alder) | 2028
83508 |  | (CN) JLL-314 Dorm 9 (JL-48 Staff Housing/Dorms) | DM | Rehang cabinet doors in dorm 10 & 17. 32" x 35" x 21" Sink Base, Cabinet, Wood, Stained | 2028
83508 |  | (CN) JLL-314 Dorm 9 (JL-48 Staff Housing/Dorms) | LMCO | Install seismic straps on the top 1/3 and the bottom 1/3 of the water heater as per IBC reference code (502.4) and UPC reference 305.1; Electric, A.O. Smith, 50 Gallon, Water Heater - Residential, Model number is ECT52210. Located in the mechanical room closet off dorm 11. | 2028
83509 |  | (CN) JLL-315 Dorm 11 (JL-49 Staff Housing/Dorms) | DM | Repair Damaged Drywall, Repair damaged drywall wall and ceiling in utility room | 2028
83509 |  | (CN) JLL-315 Dorm 11 (JL-49 Staff Housing/Dorms) | DM | Repair Damaged Drywall, Repair damaged drywall wall and ceiling in utility room | 2028
83509 |  | (CN) JLL-315 Dorm 11 (JL-49 Staff Housing/Dorms) | LMCO | Provide Clasp for Electrical Panel, Provide clasp for electrical panel in utility room per NEC Reference code 408.38; 16" x 44" Metal Panel Box, Main Electrical Service Panel, 30 Breakers, 125 Amp/3 Wire System Trumbull electric. | 2028
83509 |  | (CN) JLL-315 Dorm 11 (JL-49 Staff Housing/Dorms) | LMFS | Provide 1 HR Fire wall in hallways; 2" x 6" Wood Framing, Drop Ceiling Assembly, | 2028
83509 |  | (CN) JLL-315 Dorm 11 (JL-49 Staff Housing/Dorms) | LMLS | Provide 1HR fire wall between dorm rooms | 2028
83510 |  | (CN) JLL-317 Dorm 2 (JL-50 Staff Housing/Dorms) | DM | Inspect for Asbestos, Exterior walls have cement board shingles, check to see if they contain asbestos; Exterior Siding Material, Lap, Painted 12 x 24" shingle pattern. Painted. Located all exterior walls. | 2028
83510 |  | (CN) JLL-317 Dorm 2 (JL-50 Staff Housing/Dorms) | DM | Investigate Possible Mold, Investigate possible mold over men's showers | 2028
83510 |  | (CN) JLL-317 Dorm 2 (JL-50 Staff Housing/Dorms) | DM | Replace Missing Face Plate, Missing front shield on baseboard heater dorm 1 | 2028
83510 |  | (CN) JLL-317 Dorm 2 (JL-50 Staff Housing/Dorms) | LMCO | Add seismic strapping, Strap both water heaters. IBC Ref Code (502.4), UPC Reference 305.1 (2” wide around the top 1/3 and the bottom 1/3); Electric, Water Heater - Commercial, A.O. Smith, 100 Gallon Model 3 EES 120 911. Serial # ah83-00879-z99. | 2028
83510 |  | (CN) JLL-317 Dorm 2 (JL-50 Staff Housing/Dorms) | LMCO | Add Emergency Lighting, Add two more emergency lights at center of corridor as per (IBC Section 1008.3.5 minimum lighting levels). Wall Mounted, with dual emergency lights, | 2028
83511 |  | (CN) JLL-318 Dorm 4 (JL-51 Staff Housing/Dorms) | DM | Reposition panic hardware and repair weather seal at base of South entry door. 36" x 80" Wood, Solid Core, with Crash Bar, Deadbolt, Painted, Exterior Entrance Door, With 19“x 21“ vision lite. and a wood 12"x80 sidelight. | 2028
83511 |  | (CN) JLL-318 Dorm 4 (JL-51 Staff Housing/Dorms) | LMCO | Add seismic strapping to the top 1/3 and bottom 1/3 of the water heater as per IBC reference code 502.4 and UPC 305.1. Electric, A.O. Smith, 100 Gallon, Water Heater - Commercial, Model 3 EES 120 911. Serial # ah83-00879-z99. | 2028
83511 |  | (CN) JLL-318 Dorm 4 (JL-51 Staff Housing/Dorms) | LMCO | Add two additional emergency lights in the corridor at mid-point each side of the divided hall. (IBC Section 1008.3.5 minimum lighting levels). Wall Mounted, with dual emergency lights, | 2028
83511 |  | (CN) JLL-318 Dorm 4 (JL-51 Staff Housing/Dorms) | RMDM | Repaint fascia board as the finish is past due; 2" x 6" Wood, Fascia Board, Painted. Located at perimeter of roof. (372 LF). | 2028
83512 |  | (CN) JLL-319 Dorm 6 (JL-52 Staff Housing/Dorms) | DM | Repair Window, Repair window that does not stay open dorm 20; 34" x 54" Vinyl, Glazed Window, Double Hung, Double Pane With aluminum screen. | 2028
83512 |  | (CN) JLL-319 Dorm 6 (JL-52 Staff Housing/Dorms) | DM | Repair Damaged Baseboard, Repair damaged baseboard in laundry room by service sink; 4" Rubber, Baseboard Trim | 2028
83512 |  | (CN) JLL-319 Dorm 6 (JL-52 Staff Housing/Dorms) | LMCO | Replace Outlets to GFCI's, change outlet in utility room by washing machine to GFCI's NEC reference code 210.8 (A) vii. | 2028
83513 |  | (CN) JLL-321 Dorm 8 (JL-53 Staff Housing/Dorms) | DM | Replace missing drywall in utility room above water heater. | 2028
83513 |  | (CN) JLL-321 Dorm 8 (JL-53 Staff Housing/Dorms) | LMCO | Add seismic straps to the top 1/3 and the bottom 1/3 of the water heaters as required by code. per IBC Ref Code (502.4), & UPC Reference 305.1. Electric, Rheem, 80 Gallon, Water Heater - Commercial, Model number is MHD85245. Serial number is 8111612387. Water includes one drain release valve at bottom. Located in the utility room. | 2028
83513 |  | (CN) JLL-321 Dorm 8 (JL-53 Staff Housing/Dorms) | LMCO | Repair he electrical panel along the south wall in the utility room that does not have a closing and latching mechanism; per NEC reference 406.5(F); 20" x 53" Metal Panel Box, Square D brand, with, 42 Breakers, 400 Amp/4 Wire System, Main Electrical Service Panel, Located along the south wall of utility room. | 2028
83514 |  | (CN) JLL-322 Dorm 10 (JL-54 Staff Housing/Dorms) | DM | Replace Roof Decking, Replace roof decking on west side at overhangs (45SF) | 2028
83514 |  | (CN) JLL-322 Dorm 10 (JL-54 Staff Housing/Dorms) | LMCO | Replace Outlets to GFCI's, Outlets in laundry need to be GFCI protected as per NEC Reference Code 210.8 (A) vii. | 2028
83515 |  | (CN) JLL- Dorm 12 (JL-55 Staff Housing/Dorms) | DM | Replace Damaged Ceiling Tiles, Repair damaged suspended ceiling in men's restroom; 24" x 24" Suspended Acoustic. | 2028
83517 |  | (CN) JLL-316 Dorm 13 (JL-57 Staff Housing/Dorms) | DM | Replenish gravel at multiple locations on north side of roof and at peak. Tar & Gravel, Roof Finish. | 2028
83517 |  | (CN) JLL-316 Dorm 13 (JL-57 Staff Housing/Dorms) | DM | Repair shower insert in dorm 16 as it has a crack on the bottom; 36" x 36" x 72" Fiberglass, Shower Surround Insert Roll in shower | 2028
83518 |  | (CN) JLL-10B1 10B2 10B3 10B4 (JL-58 Staff Housing 4-Plex | DM | Replace casement hardware on rear bath window of unit 10B-3.22" x 22" Wood, Glazed Window, Casement, Double Pane, Painted with aluminum screen | 2028
83518 |  | (CN) JLL-10B1 10B2 10B3 10B4 (JL-58 Staff Housing 4-Plex | LMCO | Replace exterior outlets with GFCI. All exterior outlets are not GFCI protected. One in front of unit 11 in front of unit two and three and one in front of laundry, as per NEC Reference code 210.8(A) vii & 210.8(B) iv. | 2028
83518 |  | (CN) JLL-10B1 10B2 10B3 10B4 (JL-58 Staff Housing 4-Plex | LMCO | Replace regular outlets in unit 3 Kitchen with GFCI outlets, as per N.E.C. 210.8 (A) vi. | 2028
83518 |  | (CN) JLL-10B1 10B2 10B3 10B4 (JL-58 Staff Housing 4-Plex | LMCO | Replace outlet behind the washer in the laundry room was not GFCI protected.as per NEC Reference Code 210.8 (A) vii. | 2028
83518 |  | (CN) JLL-10B1 10B2 10B3 10B4 (JL-58 Staff Housing 4-Plex | LMLS | Replace GFCI outlet in unit four next to the stove does not trip when tested. | 2028
83518 |  | (CN) JLL-10B1 10B2 10B3 10B4 (JL-58 Staff Housing 4-Plex | LMLS | Replace missing plate cover. Unit three, right side of sink. | 2028
84979 |  | (CN) ML - CBV RV Park, Store, and Laundry | CRDM | Replace parking stops as they are past their useful life. 10" diameter Wood Timber, Parking Stop, 10' long. With a concrete 12“ x 12“ x 12“ anchor at each end. Located at site H 64, J81, J96. | 2028
84979 |  | (CN) ML - CBV RV Park, Store, and Laundry | CRDM | Replace logs as they are passed end of their useful life; 8" Curb & Gutter, logs on either side of culvert holding asphalt together. Held together with bailing wire. 4 feet long. Located at culvert behind laundry building. | 2028
84979 |  | (CN) ML - CBV RV Park, Store, and Laundry | CRDM | Replace as it is beyond its useful life; 4" x 7" Halogen, Single Bulb, Flood Light, fixture with adjustable base; Located at Loop F sign, H sign, J sign, B sign, sites 12-19 sign, site 20-22 sign | 2028
84979 |  | (CN) ML - CBV RV Park, Store, and Laundry | DM | Replace 8-inch post holding sign as it is past and of useful life. 8" diameter Wood Timber, Painted, Sign Pole, 5' post, 24"x12" sign with Routed lettering which reads “please use walks". Located at end of loop P. | 2028
84979 |  | (CN) ML - CBV RV Park, Store, and Laundry | DM | Replace signpost trailer sites two through six signs. Post is rotted at both base and along entire length. | 2028
84979 |  | (CN) ML - CBV RV Park, Store, and Laundry | DM | Secure loose 220 V receptacle at campsite E53. 7" x 15" Metal, with electrical breakers and outlets, RV Standard Power Box, Contains 1 20-amp fuse, 1 50-amp fuse, 1 30-amp fuse, one GFCI 110 outlet receptacle, 125 V receptacle, and one 250 V receptacle. Mounted to metal sleeve which is 39 inches high which is in turn mounted to concrete anchor 18 inches in diameter and 2 feet deep. | 2028
84979 |  | (CN) ML - CBV RV Park, Store, and Laundry | LMLS | Replace damaged Light fixture at entry sign to loop F, H, J, A loop trailer sites 20- 22, lights are damaged and have exposed wiring; | 2028
84980 |  | (CN) CBV-306 Employee RV, Dorm, and Service Station Area | CRDM | Replace as it is past it's useful life; Wood Timber, Retaining Wall Three-tiered planter retaining wall. With unevenly sized timbers (10" diameter average) (132 LF total) held in place by rebar stakes spaced every 9 ft. (48 LF). Each row is 4 feet wide and 36 feet long. located in front of cocktail hill comfort station | 2028
84980 |  | (CN) CBV-306 Employee RV, Dorm, and Service Station Area | DM | Replace post at cocktail hill sign with proper 6-inch diameter post | 2028
84980 |  | (CN) CBV-306 Employee RV, Dorm, and Service Station Area | DM | Repair light fixture that is missing top at South of service station | 2028
84980 |  | (CN) CBV-306 Employee RV, Dorm, and Service Station Area | DM | Repair light fixture as it is missing weather guard at three locations near service station | 2028
84980 |  | (CN) CBV-306 Employee RV, Dorm, and Service Station Area | DM | Remove tree from electrical panel array located behind site six. Tree is growing around panel so that it cannot be opened. | 2028
84980 |  | (CN) CBV-306 Employee RV, Dorm, and Service Station Area | DM | Remove abandoned electrical system between sites 51 and 72. | 2028
84980 |  | (CN) CBV-306 Employee RV, Dorm, and Service Station Area | RMDM | Replenish gravel in front of 1A-17A rest room as it is beyond end of useful life. | 2028
110229 |  | (CN) CBV-026 Elk Island Out Houses | DM | Repair gutter that has come undone from the clips that is located on the east side of the building | 2028
110229 |  | (CN) CBV-026 Elk Island Out Houses | LMAC | Replace grab bar behind the water closet so that it is a minimum of 12" to the centerline of the toilet on one side and a minimum of 24" long, as per ADAABAG Section 604.5.2; 1-1/2" diameter Grab Bar, Located behind the toilet in both outhouses | 2028
110231 |  | (CN) ML - Jackson Lake Lodge Maintained Landscape | CRDM | Replace loading ramp as it is past its useful life; Wood Slats, Fencing Enclosure, Loading chute. Constructed of 10-inch diameter posts proximately 12 feet long (55 LF) with seven 4-inch diameter rails each side (175 LF). Deck planking of three by eights (126 LF) with 2 x 4 treads (32 LF). 2 x 12 end (7 LF) with 4’ 4x4 support post. Ramp is approximately 12 feet long by 7 feet wide with a height increase of 4 feet. Currently supported by pile of railroad ties. Located at east end of East corral | 2028
110231 |  | (CN) ML - Jackson Lake Lodge Maintained Landscape | DM | Repair damage retaining wall behind dorm nine for approximately 30 linear feet | 2028
110231 |  | (CN) ML - Jackson Lake Lodge Maintained Landscape | DM | Replace deteriorated asphalt walkway in front of employee rec Hall | 2028
110231 |  | (CN) ML - Jackson Lake Lodge Maintained Landscape | DM | Replace dilapidated asphalt walkway behind dorm 1; .5' x 1848' Asphalt, Walkway | 2028
110231 |  | (CN) ML - Jackson Lake Lodge Maintained Landscape | DM | Repair deteriorated walkway at dorm 11 parking. | 2028
110231 |  | (CN) ML - Jackson Lake Lodge Maintained Landscape | DM | Repair deteriorated walkway at dorm nine parking | 2028
110231 |  | (CN) ML - Jackson Lake Lodge Maintained Landscape | DM | Repair deteriorated walkway in front of dorm two | 2028
110231 |  | (CN) ML - Jackson Lake Lodge Maintained Landscape | DM | Repair walkway surface beside pool near flagpoles for approximately 20 linear feet as it is severely deteriorated | 2028
110231 |  | (CN) ML - Jackson Lake Lodge Maintained Landscape | DM | Repair three posts (30 LF) of enclosure fence at west side of enclosure as they are beyond end of useful life. | 2028
110231 |  | (CN) ML - Jackson Lake Lodge Maintained Landscape | DM | Replace missing light fixture on light pole to north of volleyball court. | 2028
110231 |  | (CN) ML - Jackson Lake Lodge Maintained Landscape | DM | Repair light fixture in the cabin 514 as it is currently secured with duct tape. | 2028
110231 |  | (CN) ML - Jackson Lake Lodge Maintained Landscape | LMCO | Replace Standard 110 outlet located in northern bench office at village office is neither GFCI protected nor encased in weatherproof box. Replace 110 outlet with GFCI protected outlet and place inside weatherproof box. | 2028
110231 |  | (CN) ML - Jackson Lake Lodge Maintained Landscape | LMCO | Replace Outlet behind Jackson Lake Lodge entry sign is not GFCI protected. Replace outlet with GFCI receptacle. | 2028
110231 |  | (CN) ML - Jackson Lake Lodge Maintained Landscape | RMDM | Replenish gravel at bus parking as it is beyond and of useful life | 2028
110231 |  | (CN) ML - Jackson Lake Lodge Maintained Landscape | RMDM | Replenish gravel at area east of tack shed as it is beyond end of useful life. | 2028
110239 |  | (CN) CBV-902 Tent Village Sites 1 & 3 | DM | Refurbish the following logs of the structure: all four vertical posts as bases are rotted; ends of 2nd and 3rd logs from top of walls beside door and opposite door 2nd, 3rd, 4th of unit 1; bottom log of wall beside door of unit three; and ends of third and fifth logs from top of wall beside door of unit three. Stacked Log, Exterior Wall Frame Assembly 8" average diameter logs, stacked 10 high | 2028
110239 |  | (CN) CBV-902 Tent Village Sites 1 & 3 | RMDM | Treat and seal stacked log walls to prolong life. Stacked Log, Exterior Wall Frame Assembly 8" average diameter logs, stacked 10 high with 3x6 base and top plates (80 LF). With 8" diameter vertical posts 7’ high at exterior corners with 1/8"x6"x24" straps embedded in concrete. Pair of 8-inch diameter logs located vertically interstitial space between units. Pair of 3 x 6“ posts, 7’ tall, located at edges of interior space of each unit (4 total). 52 LF of wall has quarter round chinking both sides. Located at log wall of each structure. | 2028
110240 |  | (CN) CBV-903 Tent Village Sites 5 & 7 | DM | Refurbish end of log third from top of wall opposite door of unit five, ends of third and fifth logs from top of wall beside door of unit seven, third log from top of wall opposite door of unit seven, fifth logs end from top of wall side door of unit five, and refurbish the bases of vertical log posts at walls besides doors of units five and seven. Exterior Wall Frame Assembly 8” average diameter logs stacked 10 high with 3x6 base and top plates (80 LF). With 8" diameter vertical posts 7’ high at exterior corners with 1/8"x6"x24" straps embedded in concrete. Pair of 8-inch diameter logs located vertically interstitial space between units. Pair of 3 x 6“ posts, 7’ tall, located at edges of interior space of each unit (4 total). 52 LF of wall has quarter round chinking both sides. Located at log wall of each structure. | 2028
110242 |  | (CN) CBV-906 Tent Village Sites 25 & 27 | DM | Replace second log from top of wall the side door of unit 25, refurbish ends of fifth and eighth from top logs of wall opposite door of unit 25, refurbish ends of second from top and bottom two logs of wall beside door of unit 27 and end of second log from top of wall opposite door of unit 27, refurbish base of vertical logs located at the ends of walls opposite and beside the door of unit 25 and of the wall beside the door of unit 27. Also remove earth from base of wall opposite door of unit 27. Stacked Log, Exterior Wall Frame Assembly 8" average diameter logs, stacked 10 high with 3x6 base and top plates (80 LF). With 8" diameter vertical posts 7’ high at exterior corners with 1/8"x6"x24" straps embedded in concrete. Pair of 8-inch diameter logs located vertically interstitial space between units. Pair of 3 x 6“ posts, 7’ tall, located at edges of interior space of each unit (4 total). 52 LF of wall has quarter round chinking both sides. Located at log wall of each structure. | 2028
110243 |  | (CN) CBV-907 Tent Village Sites 29 & 31 | DM | Refurbish end of second and third logs from top of wall beside door of unit 31, ends of second and third logs from top of wall opposite door of unit 31, ends of second and bottom log of wall beside door of unit 29 and bases of all four vertical logs and of vertical logs making up interstitial wall. Stacked Log, Exterior Wall Frame Assembly 8" average diameter logs, stacked 10 high with 3x6 base and top plates (80 LF). With 8" diameter vertical posts 7’ high at exterior corners with 1/8"x6"x24" straps embedded in concrete. Pair of 8 inch diameter logs located vertically interstitial space between units. Pair of 3 x 6“ posts, 7’ tall, located at edges of interior space of each unit (4 total). 52 LF of wall has quarter round chinking both sides. Located at log wall of each structure. | 2028
110244 |  | (CN) CBV-909 Tent Village Sites 37 & 39 | DM | Refurbish end of second and third logs from top of wall beside door of unit 39, fourth log from top of wall opposite door of unit 39, end of fifth log from top of wall beside door of unit 37 and refurbish bases of all four vertical logs and logs making up interstitial wall. Replace second log from top of wall opposite door unit 39, replace bottom log of wall beside door of unit 39. Stacked Log, Exterior Wall Frame Assembly 8" average diameter logs, stacked 10 high with 3x6 base and top plates (80 LF). With 8" diameter vertical posts 7’ high at exterior corners with 1/8"x6"x24" straps embedded in concrete. Pair of 8-inch diameter logs located vertically interstitial space between units. Pair of 3 x 6“ posts, 7’ tall, located at edges of interior space of each unit (4 total). 52 LF of wall has quarter round chinking both sides. Located at log wall of each structure. | 2028
110245 |  | (CN) CBV-910 Tent Village Sites 2 & 4 | DM | Replace second log from top of wall beside door on unit four, refurbish end of third log from top of wall the side door of unit four, end of second log from top of wall beside door of unit two, and refurbish three of the four vertical log posts as ends are rotted except vertical post at wall opposite door of unit two. Stacked Log, Exterior Wall Frame Assembly 8" average diameter logs, stacked 10 high with 3x6 base and top plates (80 LF). With 8" diameter vertical posts 7’ high at exterior corners with 1/8"x6"x24" straps embedded in concrete. Pair of 8-inch diameter logs located vertically interstitial space between units. Pair of 3 x 6“ posts, 7’ tall, located at edges of interior space of each unit (4 total). 52 LF of wall has quarter round chinking both sides. Located at log wall of each structure. | 2028
110246 |  | (CN) CBV-908 Tent Village Sites 33 & 35 | DM | Replace second log from top of wall beside door at unit 35, refurbish ends of second, third, fourth, and fifth logs from top of wall opposite door of unit 35, refurbish ends of second and fifth logs from top of wall beside door of unit 33, refurbish end of second log from top of wall opposite door of unit 33 and refurbish bases of all four vertical logs as well as logs which make up interstitial wall. | 2028
110246 |  | (CN) CBV-908 Tent Village Sites 33 & 35 | DM | Stacked Log, Exterior Wall Frame Assembly 8" average diameter logs, stacked 10 high with 3x6 base and top plates (80 LF). With 8" diameter vertical posts 7’ high at exterior corners with 1/8"x6"x24" straps embedded in concrete. Pair of 8-inch diameter logs located vertically interstitial space between units. Pair of 3 x 6“ posts, 7’ tall, located at edges of interior space of each unit (4 total). 52 LF of wall has quarter round chinking both sides. Located at log wall of each structure. | 2028
110247 |  | (CN) CBV-911 Tent Village Sites 6 & 8 | DM | Replace bottom log of wall opposite door at unit six, refurbish ends of second and fourth logs from top of wall beside door of unit eight, refurbish bottom of all for blog posts and top of log post located at wall opposite door of unit six, and refurbish second log from top of wall the side door of unit six. | 2028
110247 |  | (CN) CBV-911 Tent Village Sites 6 & 8 | DM | Stacked Log, Exterior Wall Frame Assembly 8" average diameter logs, stacked 10 high with 3x6 base and top plates (80 LF). With 8" diameter vertical posts 7’ high at exterior corners with 1/8"x6"x24" straps embedded in concrete. Pair of 8-inch diameter logs located vertically interstitial space between units. Pair of 3 x 6“ posts, 7’ tall, located at edges of interior space of each unit (4 total). 52 LF of wall has quarter round chinking both sides. Located at log wall of each structure. | 2028
110248 |  | (CN) CBV-912 Tent Village Sites 10 & 12 | DM | Replace fifth log from top of wall opposite door of unit 12, refurbish end of third one from top of wall the side door at end near interstitial wall of unit 12, refurbish bases of all four posts and top of post on wall beside door of unit 10, refurbish ends of second third and fourth logs from top of wall beside door at unit 10 and refurbish bases of posts at interstitial wall. Stacked Log, Exterior Wall Frame Assembly 8" average diameter logs, stacked 10 high with 3x6 base and top plates (80 LF). With 8" diameter vertical posts 7’ high at exterior corners with 1/8"x6"x24" straps embedded in concrete. Pair of 8-inch diameter logs located vertically interstitial space between units. Pair of 3 x 6“ posts, 7’ tall, located at edges of interior space of each unit (4 total). 52 LF of wall has quarter round chinking both sides. Located at log wall of each structure. | 2028
110249 |  | (CN) CBV-913 Tent Village Sites 14 & 16 | DM | Replace bottom log of wall beside door of unit 14, refurbish end of second third fourth fifth sixth and seventh logs from top at wall beside door of unit 14 and 3rd log from top of wall opposite door of unit 14, refurbish ends of second third fourth and fifth logs from top at Wall opposite door unit 16 and ends of second and third box from top on the wall beside door unit 16, refurbish bases of all four vertical posts as they are rotted through. Stacked Log, Exterior Wall Frame Assembly 8" average diameter logs, stacked 10 high with 3x6 base and top plates (80 LF). With 8" diameter vertical posts 7’ high at exterior corners with 1/8"x6"x24" straps embedded in concrete. Pair of 8-inch diameter logs located vertically interstitial space between units. Pair of 3 x 6“ posts, 7’ tall, located at edges of interior space of each unit (4 total). 52 LF of wall has quarter round chinking both sides. Located at log wall of each structure. | 2028
110251 |  | (CN) CBV-915 Tent Village Sites 22 & 24 | DM | Refurbish end of second, third, fifth, ninth, and 10th logs from top of wall beside door of unit 22, refurbish ends of third and fifth logs from top of wall beside door of unit 24 and ends of second, third, fourth, and sixth log from top of wall opposite door of unit 24. Refurbish bases of all four vertical logs and of vertical logs making up interstitial wall. Stacked Log, Exterior Wall Frame Assembly 8" average diameter logs, stacked 10 high with 3x6 base and top plates (80 LF). With 8" diameter vertical posts 7’ high at exterior corners with 1/8"x6"x24" straps embedded in concrete. Pair of 8-inch diameter logs located vertically interstitial space between units. Pair of 3 x 6“ posts, 7’ tall, located at edges of interior space of each unit (4 total). 52 LF of wall has quarter round chinking both sides. Located at log wall of each structure. | 2028
110252 |  | (CN) CBV-916 Tent Village Sites 26 & 28 | DM | Refurbish end of bottom log of wall beside door of unit 26, refurbish ends of second and fourth logs from top of wall beside door of unit 28 and end of second and third logs from top of wall opposite door of unit 28. Refurbish The bases of the vertical posts located at the walls opposite the doors of units 26 and 28 and at the wall beside the door of unit 26. Stacked Log, Exterior Wall Frame Assembly 8" average diameter logs, stacked 10 high with 3x6 base and top plates (80 LF). With 8" diameter vertical posts 7’ high at exterior corners with 1/8"x6"x24" straps embedded in concrete. Pair of 8-inch diameter logs located vertically interstitial space between units. Pair of 3 x 6“ posts, 7’ tall, located at edges of interior space of each unit (4 total). 52 LF of wall has quarter round chinking both sides. Located at log wall of each structure. | 2028
110253 |  | (CN) CBV-917 Tent Village Sites 30 & 32 | DM | Replace second log from top of wall side door of unit 32, refurbish ends of second, third and sixth Logs from top of wall beside door of unit 30, refurbish ends of third, fourth, and seventh logs from top of wall opposite door of unit 32 and ends of third, fourth, and bottom logs of wall beside door of unit 32. Refurbish bases of all four log posts. Stacked Log, Exterior Wall Frame Assembly 8" average diameter logs, stacked 10 high with 3x6 base and top plates (80 LF). With 8" diameter vertical posts 7’ high at exterior corners with 1/8"x6"x24" straps embedded in concrete. Pair of 8-inch diameter logs located vertically interstitial space between units. Pair of 3 x 6“ posts, 7’ tall, located at edges of interior space of each unit (4 total). 52 LF of wall has quarter round chinking both sides. Located at log wall of each structure. | 2028
110254 |  | (CN) CBV-918 Tent Village Sites 101 & 103 | RMDM | Seal and treat stacked log walls to prolong life. | 2028
110257 |  | (CN) CBV-921 Tent Village Sites 143 & 145 | DM | Repair wall of unit 139 at entry as fifth through eighth logs have collapsed and are no longer at their 45° positions. Stacked Log, Exterior Wall Frame Assembly 4"x4" notched bottom edge turned 45 degrees stacked 17 logs tall. (80 LF) With sixteen 4"x6" posts 8’ tall set-in concrete base and ten 4"x6" posts 6.5’ tall as mid supports. Posts are bolted to wall. With 2"x14" cap with curved top mounted to peak of wall. Located at exterior log walls. | 2028
110262 |  | (CN) CBV-926 Tent Village Sites 118 & 120 | LMAC | Provide 10" of smooth surface extending the full width of the bottom of the push side of the door as per ADAABAG Section 404.2.10; 30" x 80" Wood, Screen Door, Painted With 4 x 4 post, pair of 2x4 posts, and 21 by 40 screened opening. Bottom plywood panel. Located at each unit. (This component is part of the historic fabric and or character feature of the building.) | 2028
110262 |  | (CN) CBV-926 Tent Village Sites 118 & 120 | LMAC | Adjust door closer so that from an open position of 90 degrees, the door will take at least 5 seconds to move to a point 12 degrees from the latch, measured to the leading edge of the door, as per ADAABAG Section 404.2.8.1; 30" x 80" Wood Screen Door, painted with 4 x 4 post, pair of 2x4 posts, and 21 by 40 screened opening. Bottom plywood panel located at each unit. (This component is part of the historic fabric and or character feature of the building.) | 2028
110263 |  | (CN) CBV-929 Tent Village Sites 130 & 132 | DM | Refurbish 4”x6” posts beside door (both sides of wall) at interior of unit 132 as bases are rotted off. Stacked Log, Exterior Wall Frame Assembly 4"x4" notched bottom edge turned 45 degrees stacked 17 logs tall. (80 LF) With sixteen 4"x6" posts, 8’ tall, set in concrete base and ten 4"x6" posts 6.5’ tall as mid supports. Posts are bolted to wall. With 2"x14" cap with curved top mounted to peak of wall. Located at exterior log walls. | 2028
110266 |  | (CN) CBV-930 Tent Village Sites 134 & 136 | DM | Refurbish top plate of wall opposite door in unit 134 at end as it is smashed and refurbish base of post at far end of unit 136 opposite door on interior side as base of post is missing. Stacked Log, Exterior Wall Frame Assembly 4"x4" notched bottom edge turned 45 degrees stacked 17 logs tall. (80 LF) With sixteen 4"x6" posts, 8’ tall, set in concrete base and ten 4"x6" posts 6.5’ tall as mid supports. Posts are bolted to wall. With 2"x14" cap with curved top mounted to peak of wall. Located at exterior log walls. | 2028
110267 |  | (CN) CBV-931 Tent Village Sites 138 & 140 | DM | Refurbish post on unit 138 wall beside door at far end of wall (toward rear of structure) on interior side as base is rotted away, refurbish in receipt both posts at end of wall opposite door of unit 140 as bases are rotted away and they are currently unseated and refurbish 4 x 4 doorpost at unit 140 as it is heavily damaged. Stacked Log, Exterior Wall Frame Assembly 4"x4" notched bottom edge turned 45 degrees stacked 17 logs tall. (80 LF) With sixteen 4"x6" posts, 8’ tall, set in concrete base and ten 4"x6" posts 6.5’ tall as mid supports. Posts are bolted to wall. With 2"x14" cap with curved top mounted to peak of wall. Located at exterior log walls. | 2028
110268 |  | (CN) CBV-932 Tent Village Sites 142 & 144 | DM | Repair damaged tube roof framing at unit 144 as it is bent and torn. Metal Tubing Canopy Construction 2" diameter galvanized steel tubing. Three trusses of 40 LF each, 3 horizontal members 25 LF each. 16 LF of post and top. Two triple posts of 21 LF each. 7 ft. of 1/4"x 3" flat members with 9 anchor bolts with welded connections. With corrugated galvanized sheet 2.5’x10’ mounted beside door. Located at each unit | 2028
110268 |  | (CN) CBV-932 Tent Village Sites 142 & 144 | DM | Repair fifth through seventh logs on end of wall beside side door of unit 142 as they have fallen and are no longer at 45°. Stacked Log, Exterior Wall Frame Assembly 4"x4" notched bottom edge turned 45 degrees stacked 17 logs tall. (80 LF) With sixteen 4"x6" posts, 8’ tall, set in concrete base and ten 4"x6" posts 6.5’ tall as mid supports. Posts are bolted to wall. With 2"x14" cap with curved top mounted to peak of wall. Located at exterior log walls. | 2028
110270 |  | (CN) CBV-934 Tent Village Sites 150 & 152 | DM | Reseat all posts at both units as they are in sufficiently secured. Stacked Log, Exterior Wall Frame Assembly 4"x4" notched bottom edge turned 45 degrees stacked 17 logs tall. (80 LF) With sixteen 4"x6" posts, 8’ tall, set in concrete base and ten 4"x6" posts 6.5’ tall as mid supports. Posts are bolted to wall. With 2"x14" cap with curved top mounted to peak of wall. Located at exterior log walls. | 2028
110270 |  | (CN) CBV-934 Tent Village Sites 150 & 152 | DM | Reseat posts at wall opposite door and at corner both sides of wall of unit 154. Stacked Log 4"x4" notched bottom edge turned 45 degrees stacked 17 logs tall. (80 LF) With sixteen 4"x6" posts, 8’ tall, set in concrete base and ten 4"x6" posts 6.5’ tall as mid supports. Posts are bolted to wall. With 2"x14" cap with curved top mounted to peak of wall. Located at exterior log walls. | 2028
110271 |  | (CN) CBV-935 Tent Village Sites 154 & 156 | DM | Repair tube roof framing at unit 154 as it is bent and torn. Metal Tubing Canopy Construction 2" diameter galvanized steel tubing. Three trusses of 40 LF each, 3 horizontal members 25 LF each. 16 LF of post and top. Two triple posts of 21 LF each. 7 ft. of 1/4"x 3" flat members with 9 anchor bolts. Welded connections. With corrugated galvanized sheet 2.5’x10’ mounted beside door. Located at each unit | 2028
110273 |  | (CN) B - Jenny Lake Campground Booth | CRDM | Replace as it is past its useful life; 16" x 12" Wall Mounted, Electric Space Heater, Located on the east wall. Electric water heater | 2028
110273 |  | (CN) B - Jenny Lake Campground Booth | CRDM | Replace as it is past its useful life; Automatic, Motion Sensor Switch, Motion sensor switch located on the exterior light under the south gable end. Switch is non-functioning | 2028
110273 |  | (CN) B - Jenny Lake Campground Booth | RMDM | Repaint plate covers at the edges of the glue Lam beams need to be repainted. As well as the portion of the glue Lam Beam that sticks out. This is to notify clearance required around shed | 2028
110274 |  | (CN) JNY-002 Corrals | DM | Replace missing front rails on south side of fenced enclosure (28 LF) Located at edge of employee area across from corral. | 2028
110276 |  | (CN) CBV-016 Corrals | CRDM | Replace as it is beyond its useful life; 6' x 4' Coated Steel, Swinging Gate, Located at Sick pen | 2028
110280 |  | (CN) B - GVCG - 502 Tool Shed | LMCO | Label electrical panel as per the NEC reference code 110.22; 15" x 22" Main Electrical Service Panel, located on east exterior elevation. | 2028
110326 |  | (CN) CBCG Loop A Sites 1-28 | DM | Replace damaged parking stop at Camp site #3. Wood Timber, Parking Stop, 10" diameter log mounted on pair of pyramid shaped concrete anchors that are 6" x 8" top and 6" x 24" at the bottom and approximately 2 feet deep, at each end of the timber stop. | 2028
110327 |  | (CN) CBCG Loop B Sites 29-50 | DM | Replace parking stops that are damaged and past their useful life located at site 40, in front of comfort station, and at site 49. 10" Wood Timber, Parking Stop, log, mounted on pair of pyramid shaped concrete anchors that have a 6" x 8" top and 6" x 24" bottom 2 feet deep at each end of the log parking stop. Located throughout Loop B sites. | 2028
110327 |  | (CN) CBCG Loop B Sites 29-50 | DM | Replace campsite markers for the following sites as they are past useful life: 37, 38, 39. 8" Wood Timber, painted sign pole. Post painted with number on top number is Routed, 3' high. | 2028
110328 |  | (CN) CBCG Loop C Sites 51-72 | DM | Repair parking stop at site 51, at comfort station. 10" wood timber parking stop, log, mounted on pair of pyramid shaped concrete anchors that have a 6" x 8" top and 6" x 24" bottom, 3 feet deep, at each end of the log parking stop. | 2028
110328 |  | (CN) CBCG Loop C Sites 51-72 | DM | Replace campsite marker at sites 54, 60, 69. 8" Wood Timber, Painted, Sign Pole, painted post with Routed number on top. 3' high. | 2028
110329 |  | (CN) CBCG Loop D Sites 73-109 | DM | Replace dilapidated parking stop past end of useful life located at loop D site 75 & 95. 10" Wood timber parking stop, log, mounted on pair of pyramid shaped concrete anchors that have a 6" x 8" top and 6" x 24" bottom, 36" deep, at each end of the log parking stop. | 2028
110329 |  | (CN) CBCG Loop D Sites 73-109 | DM | Replace campsite marker past end of useful life at campsite 82 and 83, 84, 98, 108. 6" Wood Timber, Painted, Sign Pole, painted post with routed number on top. 3' tall. | 2028
110330 |  | (CN) CBCG Loop E Sites 110-125 | CRDM | Replace campsite marker past end of useful life, 117, 119, 121. 8" Wood Timber, Painted, Sign Pole, painted post with routed number on top. 3' tall. Located at campsites 117, 119, & 121. | 2028
110331 |  | (CN) CBCG Loop F Sites 126-137 | DM | Replace damaged campsite marker 121 & 130; 8" Wood Timber, Painted, Sign Pole, painted post with Routed number on top. 3' tall. Located at campsites 121 &130. | 2028
110332 |  | (CN) CBCG Loop G Sites 138-149 | CRDM | Replace campsite markers as it is past end of useful life at campsite 139 and 141. 8" wood timber painted sign pole. Painted post with routed number on top. 3' tall. Located at campsites 137 & 139. | 2028
110333 |  | (CN) CBCG Loop H Sites 150-166 | DM | Replace broken post at sign. 8" wood timber painted, sign pole, double post, 36" tall, with a mounted 23" x 11" wood routed sign “Do Not Enter”. Located at end of loop. | 2028
110334 |  | (CN) CBCG Loop I Sites 167-179 | DM | Repair parking stop at site 173, 174. 10" wood timber, parking stop, log, mounted on pair of pyramid shaped concrete anchors that have a 6" x 8" top and 6" x 24" bottom, 36" deep, at each end of the log parking stop. Located throughout Loop D sites. | 2028
110334 |  | (CN) CBCG Loop I Sites 167-179 | DM | Replace bollard that is past end of useful life located at site 172, 175, 176, 179. 8" x 36" Wood, Bollards | 2028
110334 |  | (CN) CBCG Loop I Sites 167-179 | DM | Replace lintel log of campsite sign as it is rotted through. 6" wood timber painted, sign pole. Post and lintel construction top log (lintel) is 88" long, posts are 60" tall including portion in the ground, with one hanging sign that measures 35“ x 23“ with routed lettering. "Loop I One Way" and one sign that is 30" x 11" with routed lettering "Sites 138-149" Located entry to Loop. | 2028
110335 |  | (CN) CBCG Loop J Sites 180-207 | DM | Replace rotted signpost. 8" Wood Timber, Painted, Sign Pole, double post, 36" tall, with a mounted 23" x 11" wood routed sign “Do Not Enter”. Located at end of loop. | 2028
110336 |  | (CN) CBCG Loop K Sites 208-231 | DM | Replace Bollard past end of useful life, site 214, 218, 220, 225 (2), 226, 228, 229 (2). 8" wood bollards approximately 36" tall, including 24" in ground. Located throughout the loop. | 2028
110336 |  | (CN) CBCG Loop K Sites 208-231 | DM | Replace posts. 8" wood timber painted sign pole, double post, 36" tall, with a mounted 23" x 11" wood routed sign “Do Not Enter”. Located at end of loop. | 2028
110337 |  | (CN) CBCG Loop L Sites 232-259 | DM | Replace damaged bollards at site 234, 235, 238, across from site 244, 248, 250 (2), 254, 259. 8" wood bollards, 36" tall, including 24" in ground length. Located throughout the loop. | 2028
110338 |  | (CN) CBCG Loop M Sites 260-287 | CRDM | Replace exit sign past end of useful life. 8" wood timber painted sign pole, double post, 36" tall, with a mounted 23" x 11" wood routed sign “Do Not Enter”. Located at end of loop M. | 2028
110338 |  | (CN) CBCG Loop M Sites 260-287 | CRDM | Replace as it is beyond its useful life; 8" wood timber painted sign pole, double post, 36" tall, with a mounted 23" x 11" wood routed sign “Do Not Enter”. Located at end of loop. | 2028
110338 |  | (CN) CBCG Loop M Sites 260-287 | DM | Replace missing parking stop at site 270, 275, 280. 10" wood timber, parking stop, log, mounted on pair of pyramid shaped concrete anchors that have a 6" x 8" top and 6" x 24" bottom, 36" deep, at each end of the log parking stop. | 2028
110338 |  | (CN) CBCG Loop M Sites 260-287 | DM | Replace bollards beyond end of useful life located at site 271, 274, two before and two at site 275 (2), 276 (2), 280 (2), 283, 287. 8" wood bollards, 36" tall including 24" in ground length. Located throughout the loop. | 2028
110339 |  | (CN) CBCG Loop N Sites 288-312 | DM | Replace parking stop past end of useful life at sites 288, 290, 298, 303. 10" wood timber parking stop log, mounted on pair of pyramid shaped concrete anchors that have a 6" x 8" top and 6" x 24" bottom, 36" deep, at each end of the log parking stop. | 2028
110341 |  | (CN) ML - GVCG - East Corridor Sites 1-43 | DM | Repair parking stop that has come loose of the anchors located at sites 4, 6, 39. 8" Wood Timber, Parking Stop, 10 ft., 2 per site, attached to (4) 12x12x12 concrete anchors by 1/2" bolts 10" long. | 2028
110341 |  | (CN) ML - GVCG - East Corridor Sites 1-43 | RMDM | Replenish depleted and missing gravel at campsite 39. 20" x 32" Gravel, 2" Deep, Parking Area, | 2028
110343 |  | (CN) ML - GVCG - Loop B Sites 90-123 | DM | Repair parking stop that which have been overturned at campsites: 92, 101. 8" Wood Timber, Parking Stop, logs 10' long, anchored to (2) 12"x12"x24" concrete anchors at each end (2) per site. | 2028
110343 |  | (CN) ML - GVCG - Loop B Sites 90-123 | DM | Replace dilapidated parking stop past end of useful life. Sites 102, 105, 115, 120 | 2028
110343 |  | (CN) ML - GVCG - Loop B Sites 90-123 | DM | Add missing parking stop at site 115; 8" diameter Wood Timber, Parking Stop, logs 10' long, anchored to (2) 12"x12"x24" concrete anchors at each end (2) per site. | 2028
110344 |  | (CN) ML - GVCG - Loop C Sites 124-167 | DM | Reset overturned parking stop. Sites 126, 142, 153, 154, 157 | 2028
110344 |  | (CN) ML - GVCG - Loop C Sites 124-167 | DM | Replace stop at end of useful life sites 142, 154, 157, 158, 165 | 2028
110345 |  | (CN) ML - GVCG - Loop D Sites 168-207 | DM | Replace parking stop at sites 172, 176 (both), 186, 196 | 2028
110345 |  | (CN) ML - GVCG - Loop D Sites 168-207 | DM | Repair damaged electrical hookups at sites 198, 197 207 | 2028
110347 |  | (CN) ML - GVCG - Loop F Sites 287-336 | DM | Straighten crooked parking stops at site 304 (both) | 2028
110348 |  | (CN) ML - GVCG - Loop G Sites 337-372 | DM | Replace missing or dilapidated parking stop at site 348, 355, 359, & 368, | 2028
115374 |  | (CN) R - Colter Bay Concession Cabin Area Roads Rte-0254ZZ | CRDM | Replace Damaged Sign, At 800 Series Rd. intersection with Main Road near cabin 801. | 2028
115374 |  | (CN) R - Colter Bay Concession Cabin Area Roads Rte-0254ZZ | DM | Replace Damage Light Fixture, On Main Road, east side of road near Cabin #801. Add bulb and fixture to light near cabin 209. | 2028
115375 |  | (CN) R - Colter Bay Tent Village/Corrals Roads Rte-0255ZZ | DM | Replace damage bollards in between tent site 105 and 108. 8" Wood, Bollards. | 2028
115379 |  | (CN) R - JENNY LAKE Cabin Access Roads Rte-0260ZZ | DM | Replace (2) missing or damaged parking stops located along cabin access road near large parking lot moving east; 10" diameter wood timber parking stop 12' long with 24"x24"x6" concrete anchors at ends. | 2028
115389 |  | (CN) R - JENNY LAKE Employee Housing Road, Rte-0444 | CRDM | Replace as it is past it's useful life; Asphalt Roadway/Street Surface, 3" deep. Located north of employee dorms, starting at Route 0260, and ending at NPS gravel service road. | 2028
115389 |  | (CN) R - JENNY LAKE Employee Housing Road, Rte-0444 | DM | Secure signage as both signs are poorly anchored | 2028
115393 |  | (CN) R - COLTER BAY Concession Store & Gas Parking, Rte-1010 | CRDM | Replace as they are past their useful life; 10" diameter Parking Stop, With (24) 8“ x 20" x 24" deep concrete anchors. Located at all 12 parking stalls. | 2028
115404 |  | (CN) R - JENNY Lake Lodge Cabin Parking, Rte-1026 | DM | Repair and secure parking stops located in south parking area and adjacent in landscape area. | 2028
115405 |  | (CN) R - JLL Lodge Clinic & Service Station Pkg, Rte-1028 | DM | Replace damaged concrete, Curb & Gutter, with rounded edging with exposed aggregate. 50 LF in the clinic/service station parking. | 2028
115405 |  | (CN) R - JLL Lodge Clinic & Service Station Pkg, Rte-1028 | RMDM | Re-stripe parking stalls as the corral parking does not have designated parking stalls properly marked. Asphalt Roadway/Street Surface, 3" Deep Includes 26 parking stalls in the corral area. Located from Main entry road to corral area. | 2028
115406 |  | (CN) R - COLTER BAY Cabin Pkg Areas, Rte 1029ZZ | DM | Repair missed placed/tipped over/misaligned parking stops located throughout various areas of the cabin parking area. Near cabin #403, at parking stall just west of restaurant loading dock, (2) #432, #436, #622, #626, | 2028
115406 |  | (CN) R - COLTER BAY Cabin Pkg Areas, Rte 1029ZZ | DM | Add missing parking stops. Add (3) at cabin #440 to 444; 10" diameter wood timber parking stop. | 2028
228281 |  | (CN) CBCG Group Sites | DM | Replace parking stops beyond and of useful life, at sites 9, 3(3), 4, 6, 7(2), D, E, F | 2028
228281 |  | (CN) CBCG Group Sites | DM | Replace damaged bollard past and of useful life at sites 1, 3, 6 (3), 7 (2), D | 2028
228281 |  | (CN) CBCG Group Sites | DM | Add missing sign at end of group loop. 23" X 11", wood timber sign pole, painted. 8" diameter wood timber painted sign pole, 3 feet long post, with 23"x11" routed lettering “Do Not Enter“. Located at end of loop. | 2028
228281 |  | (CN) CBCG Group Sites | DM | Replace damaged sign at group Loops three and four | 2028
234154 |  | (CN) CBV Employee RV Park Restroom | LMCO | Add Seismic strapping shall be 2” wide around the top 1/3 and the bottom 1/3 as per UPC (Uniformed Plumbing Code) Reference 507.2; Electric Water Heater - Residential, A.O. Smith, 120 Gallon Model #PEC-120-M202172000. Located in the utility chase | 2028
234154 |  | (CN) CBV Employee RV Park Restroom | LMCO | Provide 30 inch clear for space in front of electrical panel. As per NEC Code Reference 110.26; 14" x 38" Metal Panel Box, Main Electrical Service Panel, Square D brand, with 42 breakers, 200 Amp/3 Wire System Located on the east wall in the utility chase. | 2028
249651 |  | (CN) B - CBCG- Comfort Station Loop J - Accessible | LMAC | Adjust grab bars so the clear space between all grab bars and walls to be 1-1/2" as per ADAABAG Section 609.3; 1-1/2" diameter Stainless Steel, Grab Bar, L-shaped Grab bar that is 7LF at Corner behind and on the side wall of the water closet. Located in men’s and women’s restrooms. | 2028
249651 |  | (CN) B - CBCG- Comfort Station Loop J - Accessible | LMAC | Adjust the self-closing valve delay so the faucet remains open for at least 10 seconds; ADAABAG Section 606.4; Chrome Finish, Faucet - Single Valve, Push valve with automatic closer. located in the men's and women's restrooms. | 2028
249651 |  | (CN) B - CBCG- Comfort Station Loop J - Accessible | LMAC | Relocate water closets located in the women's accessible stall so the center line of the water closet is between 16"-18" from the closest wall, as per ADAABAG Section 604.2. Porcelain, with Tank, Floor Mounted, with Manual Handle Flush Valve, Water Closet, | 2028
249653 |  | (CN) UT - Jenny Lake Campground Water System | DM | Repair non-working hose bib near campsite 44. Hose bib, pump style. | 2028
249653 |  | (CN) UT - Jenny Lake Campground Water System | DM | Replace damaged and rotted posts at hose bibs near campsites 15, 23, & 29. 4" x 4" Wood, Bollards. | 2028
249658 |  | (CN) ML - JNY Maintained Landscape | DM | Replace parking stop as it is damaged. Located the side cabin geranium, at employee parking near corral, and beside pathway entry to south of lodge parking area. 36 LF. | 2028
249658 |  | (CN) ML - JNY Maintained Landscape | DM | Repair wash out in asphalt pavement at cabin Goldenrod; asphalt parking area. | 2028
249658 |  | (CN) ML - JNY Maintained Landscape | DM | Replace rotted posts as they are past end of useful life located at welcome sign beside flagpole. (12 LF) | 2028
249658 |  | (CN) ML - JNY Maintained Landscape | DM | Replace sign support post as it is past and of useful life. 72" x 33" wood timber sign pole painted. Hanging sign assembly with routed lettering, mounted to 10-inch diameter post. post and lintel assembly. Posts are approximately 10 feet tall each and lintel is approximately 10 feet at entry to lodge area | 2028
249658 |  | (CN) ML - JNY Maintained Landscape | RMDM | Replenish gravel at end of useful life | 2028
249658 |  | (CN) ML - JNY Maintained Landscape | RMDM | Replenish gravel as it is beyond end of useful life; 5' gravel walkway located between cabin area and corral area. 300 LF | 2028
249658 |  | (CN) ML - JNY Maintained Landscape | RMDM | Refinish walkway lights as varnish is beginning to decay | 2028
249658 |  | (CN) ML - JNY Maintained Landscape | RMDM | Replenish gravel throughout employee area as it is past end of useful life; gravel walkway located throughout employee area. | 2028
249658 |  | (CN) ML - JNY Maintained Landscape | RMDM | Replenish gravel to rear of employee area as it is past end of useful life; gravel parking area located to rear and side of employee area and behind lodge. | 2028
249684 |  | (CN) UT - JNY Waste Water System | DM | Move warning flashing red light to the exterior of the cabin so it can be seen if there is a problem; EG pump control panel with a 35"x42" metal box with flashing red light on top of lift station pumps Factory # 249592, Voltage 230V, with 2-1/6 hp motors. Located in the utility room of FMSS #83370. | 2028
249713 |  | (CN) ML - GVCG - Concessions Employee Area and Office | CRDM | Replace dilapidated stairs located between office and employee RV area as they are beyond end of useful life. Stairs, Wood, 5 rise, 20x27", 7" rise. 2x10 construction. Painted. At path to employee area behind office. | 2028
249713 |  | (CN) ML - GVCG - Concessions Employee Area and Office | LMCO | Repair Breakers in panel nearest the office are improperly linked with piece of wire, remedy immediately, as per NEC Code Reference 240.15 (B)(1). | 2028
249723 |  | (CN) ML - CB Cabins, Restaurants, and Trailer Parking Area | CRDM | Replace parking stops past end of useful life. 10" diameter Wood Timber, Parking Stop, 10 feet long, With a 12" x 12" x 36“ concrete anchor at each end. Located throughout overflow parking area. | 2028
249723 |  | (CN) ML - CB Cabins, Restaurants, and Trailer Parking Area | CRDM | Replace as it is beyond its useful life; Stairs, Railroad tie stairs leading from parking area to cabin 413, stairs have 12 treads and 12 risers. Stairs are 5 feet wide. Risers are 3 inches tall. Treads are14 inches deep with dirt infill. 94 LF of Railroad Tie. Located from parking area to cabin 413. | 2028
249723 |  | (CN) ML - CB Cabins, Restaurants, and Trailer Parking Area | CRDM | Replace stairs at cabin 634 as they are at end of useful life. Stairs, constructed of 2" x 6" treated members at sides and nosing (78 LF) with asphalt infill, treads are on average 48 inches x 28 inches. Quarter turn design, there are eight treads and nine rises. Rises are approximately 6 inches. Corners are held together with steel plates. Located from parking lot to cabin 634 and 633. | 2028
249723 |  | (CN) ML - CB Cabins, Restaurants, and Trailer Parking Area | CRDM | Replace as it is beyond its useful life; Stairs, Stairs constructed of 4" x 6" Timbers at sides and nosing (31LF). Treads are 20" x 36". There are four treads. There are five risers. Risers are 4 inches. Treads are asphalt infill. Located at cabin 613 | 2028
249723 |  | (CN) ML - CB Cabins, Restaurants, and Trailer Parking Area | CRDM | Replace post as the bottoms are rotted off. 12'' X 7', wood slat fencing painted, with painted 4 x 8 posts, 3-inch log slats, center post is tripled two by eights, top and bottom rail are 2 x 4. Located next to cabin office. | 2028
249723 |  | (CN) ML - CB Cabins, Restaurants, and Trailer Parking Area | CRDM | Replace fencing structure as it is at end of useful life. Structure is in process of collapse including wood slats, top rail and corner supports. Fencing, with 8-inch diameter posts at ends and middle approximately 8 feet high including in ground portion of post. Has 8 foot long upper and lower rails, with 1"x6" slats. Located across from restaurant in front of cabin 233. | 2028
249723 |  | (CN) ML - CB Cabins, Restaurants, and Trailer Parking Area | CRDM | Replace as it is beyond its useful life; 8" diameter Wood Timber, Painted, Sign Pole, 5-foot post with 34“ x 22“ sign with routed lettering labeled "seasonal boat trailer parking". Located at entry to boat parking | 2028
249723 |  | (CN) ML - CB Cabins, Restaurants, and Trailer Parking Area | DM | Replace missing asphalt to right of the cabin office | 2028
249723 |  | (CN) ML - CB Cabins, Restaurants, and Trailer Parking Area | DM | Replace damaged asphalt outside Cabin 203. | 2028
249723 |  | (CN) ML - CB Cabins, Restaurants, and Trailer Parking Area | DM | Repair damaged asphalt walkway or walkway has settled approximately 7 inches at cabin 806 and cabin 831. | 2028
249723 |  | (CN) ML - CB Cabins, Restaurants, and Trailer Parking Area | DM | Repair missing asphalt on pathway by cabin 417 leading to road above cabin | 2028
249723 |  | (CN) ML - CB Cabins, Restaurants, and Trailer Parking Area | DM | Repair asphalt heaved up by roots near cabin 229, cabin 1009 | 2028
249723 |  | (CN) ML - CB Cabins, Restaurants, and Trailer Parking Area | DM | Repair heaved and missing walkway near cabin 233 | 2028
249723 |  | (CN) ML - CB Cabins, Restaurants, and Trailer Parking Area | DM | Repair damaged asphalt to left of cabin 492 | 2028
249723 |  | (CN) ML - CB Cabins, Restaurants, and Trailer Parking Area | DM | Replace missing section asphalt path beside cabin 624. Section is approximately 30 feet long | 2028
249723 |  | (CN) ML - CB Cabins, Restaurants, and Trailer Parking Area | DM | Re-level gate 18'' X 4', Coated Steel, Swinging Gate, Painted, Located at boat parking | 2028
249723 |  | (CN) ML - CB Cabins, Restaurants, and Trailer Parking Area | DM | Straighten loose bollards located at uphill entry to overflow parking. | 2028
249723 |  | (CN) ML - CB Cabins, Restaurants, and Trailer Parking Area | DM | Replace missing bollard located at west entrance to overflow parking | 2028
249723 |  | (CN) ML - CB Cabins, Restaurants, and Trailer Parking Area | DM | Replace sign lintel as it is destroyed. 8" diameter wood timber painted sign pole. Post and lintel construction with 4-foot posts and 68" lintel, with 34“ x 22“ routed lettered sign. Located at entry to office area. | 2028
249723 |  | (CN) ML - CB Cabins, Restaurants, and Trailer Parking Area | RMDM | Replace damaged asphalt outside cabin 205 at entire walkway | 2028
249723 |  | (CN) ML - CB Cabins, Restaurants, and Trailer Parking Area | RMDM | Repaint gate 18'' X 4', Coated Steel, Swinging Gate, Painted, Located at boat parking | 2028
249731 |  | (CN) ML - CBV Marina Maintained Landscape | DM | Repair trail wash out behind and to the side of Marina Office. 4'' X 250', asphalt walkway, 2-1/2" Deep, located between side entrance of marina office and parking | 2028
249731 |  | (CN) ML - CBV Marina Maintained Landscape | DM | Repair washout area in sidewalk to comfort station from parking area | 2028
249732 |  | (CN) ML - Tent Village Maintained Landscape | DM | Replace damaged parking stop at sites 105/107, 134, 150, 142/144, and 146; wood timber parking stop 10" diameter 10’ long with pair of concrete anchors 8"x24"x24". | 2028
249732 |  | (CN) ML - Tent Village Maintained Landscape | DM | Replace damaged bollard at sites: 154/156, 101/103, 102/104, 112, 110, 138/140, 144, 146 | 2028
249732 |  | (CN) ML - Tent Village Maintained Landscape | DM | Replace pole for campsite marker signs at the following sites: 1, 2, 10, 11, 18, 31, 103, 102, 104, 114, 116, 120, 124, 126, 128, 134, 140, 142, 143 | 2028
249732 |  | (CN) ML - Tent Village Maintained Landscape | DM | Replace missing sign at site 20; 10" x 5" wood timber sign pole painted with routed number for campsite, mounted to 4-inch diameter pole approximately 3 feet long. | 2028
249732 |  | (CN) ML - Tent Village Maintained Landscape | DM | Replace fire extinguisher mounting pole near sites 2, 9, 11, 37, 110, 150, 154 (base rotted through). | 2028
249746 |  | (CN) UT - CBV Concessioner Water System | DM | Adjust the height of hose bib on site B-27 so that it is between 28"-36" above the ground as per Outdoor Developed Area Report 16.16.3; Brass, lever style, ball valve, Hose bib | 2028
249746 |  | (CN) UT - CBV Concessioner Water System | DM | Adjust the force required to operate the hose bib to be no greater than 5 pounds of force as per Outdoor Developed Area Report 16.16.1; Brass, lever style, ball valve, Hose bib located at the (7) Accessible sites. | 2028