## Sheet1
LOCATION | ASSET CODE | ASSET DESCRIPTION | WORK SUBTYPE | WORK ORDER DESCRIPTION | QTY | UOM
Log Cabin | 82011 | CBldg 621 Lake Crescent Log Cabin Resort Laundry Linen House | LMLS | Replace Lighting & Branch Wiring - General - receptacles, 687 S.F., correct wiring deficiencies in the shed to ensure all wiring meets code. | 1 | EA
Log Cabin | 82013 | CBldg 1471 Lake Crescent Log Cabin Resort RV CS & Laundromat | CRDM | Replace Roof Covering - Gutters, 48 L.F., Eaves | 24 | SF
Log Cabin | 82013 | CBldg 1471 Lake Crescent Log Cabin Resort RV CS & Laundromat | CRDM | Replace Roof Covering - Downspouts, 20 V.L.F., Building corners | 10 | SF
Log Cabin | 82013 | CBldg 1471 Lake Crescent Log Cabin Resort RV CS & Laundromat | CRDM | Replace Distribution System - Fan System, Residential bath exhaust, 100 CFM, Restrooms and Laundry Room | 3 | EA
Log Cabin | 82013 | CBldg 1471 Lake Crescent Log Cabin Resort RV CS & Laundromat | CRDM | Replace Terminal & Package Unit - 208-240 volt, 5 kW, Restrooms and Laundry Room | 3 | EA
Log Cabin | 82013 | CBldg 1471 Lake Crescent Log Cabin Resort RV CS & Laundromat | CRDM | Replace Lighting & Branch Wiring - General - receptacles, 900 S.F., Throughout building | 1 | EA
Log Cabin | 82013 | CBldg 1471 Lake Crescent Log Cabin Resort RV CS & Laundromat | CRDM | Replace Lighting & Branch Wiring - Exterior Lighting - Incandescent, wall mounted, 100 W, Exterior near Restrooms and Mechanical Space Doors | 3 | EA
Log Cabin | 82013 | CBldg 1471 Lake Crescent Log Cabin Resort RV CS & Laundromat | CRDM | Replace Lighting & Branch Wiring - Interior Lighting, FL - 4 Lamp T8, Laundry Room | 3 | EA
Log Cabin | 82013 | CBldg 1471 Lake Crescent Log Cabin Resort RV CS & Laundromat | CRDM | Replace Lighting & Branch Wiring - Interior Lighting, Fluorescent - Surface Mounted (Type B), Restrooms | 6 | EA
Log Cabin | 82013 | CBldg 1471 Lake Crescent Log Cabin Resort RV CS & Laundromat | CRDM | Replace Lighting & Branch Wiring - Interior Lighting, Incandescent, Mechanical space | 2 | EA
Log Cabin | 82022 | CBldg 869 Lake Crescent Log Cabin Resort Maint/Marine | RMDM | Clean and refinish 360 sf of wood plank siding. | 360 | SF
Log Cabin | 82023 | CBldg 872 Lake Crescent Log Cabin Resort Lodge/Motel Rooms 1 | CRDM | Replace Wall Finishes - Tile, Office closet | 234 | SF
Log Cabin | 82023 | CBldg 872 Lake Crescent Log Cabin Resort Lodge/Motel Rooms 1 | CRDM | Replace Integrated Construction - Cold Storage Room, Walk-in refrigerator/freezer, 7'-3"x5'-4", 40 S.F., Kitchen Dry Storage Room | 1 | EA
Log Cabin | 82023 | CBldg 872 Lake Crescent Log Cabin Resort Lodge/Motel Rooms 1 | DM | Demo and rebuild furnace/boiler room, between kitchen area and comfort station; exterior walls | 192 | SF
Log Cabin | 82023 | CBldg 872 Lake Crescent Log Cabin Resort Lodge/Motel Rooms 1 | RMDM | Prep and refinish Exterior Doors - Exterior door, 3' by 7', Painted or coated, 2 Opng., North side to office and south side to store/snack bar | 2 | EA
Log Cabin | 82023 | CBldg 872 Lake Crescent Log Cabin Resort Lodge/Motel Rooms 1 | RMDM | Prep and refinish Exterior Doors - Exterior glazed door, wood frame, single, 3' by 7', Painted or coated, 1 Opng., South side to store | 1 | EA
Log Cabin | 82023 | CBldg 872 Lake Crescent Log Cabin Resort Lodge/Motel Rooms 1 | RMDM | Prep and refinish Exterior Doors - Exterior glazed door, wood frame, double, 3' by 7', Painted or coated, 4 Opng., Main entrance and dining entrance from the south side patio | 4 | EA
Log Cabin | 82023 | CBldg 872 Lake Crescent Log Cabin Resort Lodge/Motel Rooms 1 | RMDM | Prep and refinish Exterior Doors - Exterior door, 1/2 glass, wood, 3' by 7', Painted or coated, Kitchen service entrance, east side | 1 | EA
Log Cabin | 82023 | CBldg 872 Lake Crescent Log Cabin Resort Lodge/Motel Rooms 1 | RMDM | Prep and refinish Interior Doors - Wood Door/Wood Frame, Swinging doors, Painted or coated, Kitchen | 3 | EA
Log Cabin | 82023 | CBldg 872 Lake Crescent Log Cabin Resort Lodge/Motel Rooms 1 | RMDM | Prep and refinish Wall Finishes - Wood, wood paneling, painted, Painted or coated, Lobby, dining, kitchen | 2750 | SF
Log Cabin | 82023 | CBldg 872 Lake Crescent Log Cabin Resort Lodge/Motel Rooms 1 | RMDM | Prep and refinish Ceiling Finishes - Wood Panel, Painted or coated, Kitchen storage and prep | 480 | SF
Log Cabin | 82024 | CBldg 1484 Lake Crescent Log Cabin Resort A-Frame Chalet Uni | CRDM | Replace Electrical Service & Distribution - Main lugs, 50 amp, Inside, near front entry doors | 6 | EA
Log Cabin | 82024 | CBldg 1484 Lake Crescent Log Cabin Resort A-Frame Chalet Uni | CRDM | Replace Lighting & Branch Wiring - General - receptacles, 2415 S.F., Throughout building | 1 | EA
Log Cabin | 82024 | CBldg 1484 Lake Crescent Log Cabin Resort A-Frame Chalet Uni | CRDM | Replace Lighting & Branch Wiring - Exterior Lighting - Incandescent, wall mounted, 100 W, Exterior near front and rear entry doors | 12 | EA
Log Cabin | 82024 | CBldg 1484 Lake Crescent Log Cabin Resort A-Frame Chalet Uni | CRDM | Replace Lighting & Branch Wiring - Interior Lighting, Incandescent, Wall sconce, Kitchen areas | 6 | EA
Log Cabin | 82024 | CBldg 1484 Lake Crescent Log Cabin Resort A-Frame Chalet Uni | CRDM | Replace Lighting & Branch Wiring - Interior Lighting, Incandescent, Wall dome light, Near loft stairs | 6 | EA
Log Cabin | 82024 | CBldg 1484 Lake Crescent Log Cabin Resort A-Frame Chalet Uni | CRDM | Replace Lighting & Branch Wiring - Interior Lighting, Incandescent, Ceiling fan with light, Main living areas | 6 | EA
Log Cabin | 82024 | CBldg 1484 Lake Crescent Log Cabin Resort A-Frame Chalet Uni | LMLS | Install 2 missing breaker blanks in this panel to remove a life safety hazard. | 1 | EA
Log Cabin | 82024 | CBldg 1484 Lake Crescent Log Cabin Resort A-Frame Chalet Uni | RMDM | Prep and refinish Roof Construction - Truss/Joist - Wood, Painted or coated, 96 S.F., entry canopies. | 1 | EA
Log Cabin | 82024 | CBldg 1484 Lake Crescent Log Cabin Resort A-Frame Chalet Uni | RMDM | Prep and refinish Roof Construction - Deck - Wood, Painted or coated, 96 S.F., entry canopies | 1 | EA
Log Cabin | 82024 | CBldg 1484 Lake Crescent Log Cabin Resort A-Frame Chalet Uni | RMDM | Prep and refinish Exterior Walls - CIP Concrete, Painted or coated, Exterior, fill cracks and spalls as needed. Approximately 60 LF of small cracks observed. | 2602 | SF
Log Cabin | 82024 | CBldg 1484 Lake Crescent Log Cabin Resort A-Frame Chalet Uni | RMDM | Prep and refinish Exterior Walls - Wood Cladding w/Stud Backup, Board & Batten, Painted or coated, Exterior. Repair or replace damaged areas as needed. Approximately 30 SF of dry rot observed in the siding and 40 LF of trim noted with dry rot. . | 1540 | SF
Log Cabin | 82024 | CBldg 1484 Lake Crescent Log Cabin Resort A-Frame Chalet Uni | RMDM | Prep and refinish Exterior Doors - Wood, 2'-6"x6'-6" composite, Painted or coated, 6 Opng., North side | 6 | EA
Log Cabin | 82024 | CBldg 1484 Lake Crescent Log Cabin Resort A-Frame Chalet Uni | RMDM | Prep and refinish Exterior Doors - Wood, 3'-6"x6'-6" composite, Painted or coated, 6 Opng., South side | 6 | EA
Log Cabin | 82024 | CBldg 1484 Lake Crescent Log Cabin Resort A-Frame Chalet Uni | RMDM | Prep and refinish Walls - Wood, planter walls, Painted or coated, North side | 376 | SF
Log Cabin | 82025 | CBldg 1485 Lake Crescent Log Cabin Resort A-Frame Chalet Eas | CRDM | Replace Electrical Service & Distribution - Main lugs, 50 amp, Inside, near front entry doors | 6 | EA
Log Cabin | 82025 | CBldg 1485 Lake Crescent Log Cabin Resort A-Frame Chalet Eas | CRDM | Replace Lighting & Branch Wiring - General - receptacles, 2415 S.F., Throughout building | 1 | EA
Log Cabin | 82025 | CBldg 1485 Lake Crescent Log Cabin Resort A-Frame Chalet Eas | CRDM | Replace Lighting & Branch Wiring - Exterior Lighting - Incandescent, wall mounted, 100 W, Exterior near front and rear entry doors | 12 | EA
Log Cabin | 82025 | CBldg 1485 Lake Crescent Log Cabin Resort A-Frame Chalet Eas | RMDM | Prep and refinish Roof Construction - Deck - Wood, Painted or coated, 96 S.F., entry canopies | 1 | EA
Log Cabin | 82025 | CBldg 1485 Lake Crescent Log Cabin Resort A-Frame Chalet Eas | RMDM | Prep and refinish Exterior Walls - CIP Concrete, Painted or coated, Exterior, fill cracks and spalls as needed. Approximately 60 LF of small cracks observed. | 2602 | SF
Log Cabin | 82025 | CBldg 1485 Lake Crescent Log Cabin Resort A-Frame Chalet Eas | RMDM | Prep and refinish Exterior Walls - Wood Cladding w/Stud Backup, Board & Batten, Painted or coated, Exterior. Repair or replace damaged areas as needed. Approximately 30 SF of dry rot observed in the siding and 40 LF of trim noted with dry rot. . | 1540 | SF
Log Cabin | 82025 | CBldg 1485 Lake Crescent Log Cabin Resort A-Frame Chalet Eas | RMDM | Prep and refinish Exterior Doors - Wood, 2'-6"x6'-6" composite, Painted or coated, 6 Opng., North side | 6 | EA
Log Cabin | 82025 | CBldg 1485 Lake Crescent Log Cabin Resort A-Frame Chalet Eas | RMDM | Prep and refinish Exterior Doors - Wood, 3'-6"x6'-6" composite, Painted or coated, 6 Opng., South side | 6 | EA
Log Cabin | 82027 | Cbldg 1527 Lake Crescent Log Cabin Resort Camping Cabin 25 | CRDM | Replace Roof Construction - Column - Wood, Round posts, 2 @ 7', 2 @ 8', Painted or coated, 30 L.F., | 1 | EA
Log Cabin | 82027 | Cbldg 1527 Lake Crescent Log Cabin Resort Camping Cabin 25 | CRDM | Replace Exterior Walls - Hand railing, Painted or coated, 30 L.F., | 30 | SF
Log Cabin | 82027 | Cbldg 1527 Lake Crescent Log Cabin Resort Camping Cabin 25 | CRDM | Replace Electrical Service & Distribution - Main lugs, 50 amp, 60A load center, | 1 | EA
Log Cabin | 82027 | Cbldg 1527 Lake Crescent Log Cabin Resort Camping Cabin 25 | CRDM | Replace Lighting & Branch Wiring - General - receptacles, 394 S.F., | 1 | EA
Log Cabin | 82027 | Cbldg 1527 Lake Crescent Log Cabin Resort Camping Cabin 25 | RMDM | Refinish 434 SF of wood plank decking inside the building and on the porch. | 1 | EA
Log Cabin | 82027 | Cbldg 1527 Lake Crescent Log Cabin Resort Camping Cabin 25 | RMDM | Clean and refinish 544 SF of exterior logs. | 544 | SF
Log Cabin | 82028 | CBldg 1528 Lake Crescent Log Cabin Resort Camping Cabin 26 | CRDM | Replace Roof Construction - Column - Wood, Round posts, 2 @ 7', 2 @ 8', Painted or coated, 30 L.F., | 1 | EA
Log Cabin | 82028 | CBldg 1528 Lake Crescent Log Cabin Resort Camping Cabin 26 | CRDM | Replace Exterior Walls - Hand railing, Painted or coated, 30 L.F., | 30 | SF
Log Cabin | 82028 | CBldg 1528 Lake Crescent Log Cabin Resort Camping Cabin 26 | CRDM | Replace Electrical Service & Distribution - Main lugs, 50 amp, 60A load center, | 1 | EA
Log Cabin | 82028 | CBldg 1528 Lake Crescent Log Cabin Resort Camping Cabin 26 | CRDM | Replace Lighting & Branch Wiring - General - receptacles, 394 S.F., | 1 | EA
Log Cabin | 82028 | CBldg 1528 Lake Crescent Log Cabin Resort Camping Cabin 26 | RMDM | Refinish 434 SF of wood plank decking inside the building. | 1 | EA
Log Cabin | 82028 | CBldg 1528 Lake Crescent Log Cabin Resort Camping Cabin 26 | RMDM | Clean and refinish 544 SF of exterior logs. | 544 | SF
Log Cabin | 82028 | CBldg 1528 Lake Crescent Log Cabin Resort Camping Cabin 26 | RMDM | Clean and refinish 230 SF of wood siding along the base of the building. | 230 | SF
Log Cabin | 82029 | CBldg 1529 Lake Crescent Log Cabin Resort Camping Cabin 27 | CRDM | Replace Roof Construction - Column - Wood, Round posts, 2 @ 7', 2 @ 8', Painted or coated, 30 L.F., | 1 | EA
Log Cabin | 82029 | CBldg 1529 Lake Crescent Log Cabin Resort Camping Cabin 27 | CRDM | Replace Exterior Walls - Hand railing, Painted or coated, 30 L.F., | 30 | SF
Log Cabin | 82029 | CBldg 1529 Lake Crescent Log Cabin Resort Camping Cabin 27 | CRDM | Replace Electrical Service & Distribution - Main lugs, 50 amp, 60A load center, | 1 | EA
Log Cabin | 82029 | CBldg 1529 Lake Crescent Log Cabin Resort Camping Cabin 27 | CRDM | Replace Lighting & Branch Wiring - General - receptacles, 394 S.F., | 1 | EA
Log Cabin | 82029 | CBldg 1529 Lake Crescent Log Cabin Resort Camping Cabin 27 | RMDM | Refinish 434 SF of wood plank decking inside the building and on the porch. | 1 | EA
Log Cabin | 82029 | CBldg 1529 Lake Crescent Log Cabin Resort Camping Cabin 27 | RMDM | Clean and refinish 544 SF of exterior logs. | 544 | SF
Log Cabin | 82029 | CBldg 1529 Lake Crescent Log Cabin Resort Camping Cabin 27 | RMDM | Clean and refinish 230 SF of wood siding along the base of the building. | 230 | SF
Log Cabin | 82030 | Cbldg 1530 Lake Crescent Log Cabin Resort Camping Cabin 28 | CRDM | Replace Roof Construction - Column - Wood, Round posts, 2 @ 7', 2 @ 8', Painted or coated, 30 L.F., | 1 | EA
Log Cabin | 82030 | Cbldg 1530 Lake Crescent Log Cabin Resort Camping Cabin 28 | CRDM | Replace Exterior Walls - Hand railing, Painted or coated, 30 L.F., | 30 | SF
Log Cabin | 82030 | Cbldg 1530 Lake Crescent Log Cabin Resort Camping Cabin 28 | CRDM | Replace Electrical Service & Distribution - Main lugs, 50 amp, 60A load center, | 1 | EA
Log Cabin | 82030 | Cbldg 1530 Lake Crescent Log Cabin Resort Camping Cabin 28 | CRDM | Replace Lighting & Branch Wiring - General - receptacles, 394 S.F., | 1 | EA
Log Cabin | 82030 | Cbldg 1530 Lake Crescent Log Cabin Resort Camping Cabin 28 | RMDM | Refinish 434 SF of wood plank decking inside the building and on the porch. | 1 | EA
Log Cabin | 82030 | Cbldg 1530 Lake Crescent Log Cabin Resort Camping Cabin 28 | RMDM | Clean and refinish 544 SF of exterior logs. | 544 | SF
Log Cabin | 82030 | Cbldg 1530 Lake Crescent Log Cabin Resort Camping Cabin 28 | RMDM | Clean and refinish 230 SF of wood siding along the base of the building. | 230 | SF
Log Cabin | 82035 | CCmpg Lake Crescent Log Cabin Resort Campground | CRDM | Replace Electrical Service & Distribution - Main lugs, 200 amp, Near campsites 7 & 8 | 1 | EA
Log Cabin | 82035 | CCmpg Lake Crescent Log Cabin Resort Campground | LMLS | Install missing breaker blanks to remove safety hazard. | 1 | EA
Fairholme | 82103 | CBldg 1314 Fairholme General Store | CRDM | Replace small wall mounted unit heater in the staff restroom at the end of its service life. | 1 | EA
Fairholme | 82103 | CBldg 1314 Fairholme General Store | DM | Reroute the north downspouts to discharge rain water runoff away from the building and prevent future damage to the wood piles. | 1 | EA
Fairholme | 82103 | CBldg 1314 Fairholme General Store | RMDM | Repaint the door every 5 years. | 1 | EA
Fairholme | 82103 | CBldg 1314 Fairholme General Store | RMDM | Repaint the doors every 5 years. | 4 | EA
Fairholme | 82103 | CBldg 1314 Fairholme General Store | RMDM | Repaint the door every 5 years. | 1 | EA
Fairholme | 82103 | CBldg 1314 Fairholme General Store | RMDM | Repaint the door every 5 years. | 1 | EA
Fairholme | 82103 | CBldg 1314 Fairholme General Store | RMDM | Repaint the doors every 5 years. | 4 | EA
Fairholme | 82104 | CBldg 1321 Fairholme Boat Rental Shed | DM | Install approximately 1 cubic yard lean concrete or flowable fill to fill void cause d by erosion. Armor corner with quarry spalls, then regrade 50 sq. feet around side of building to direct storm water away from building. | 50 | SF
Fairholme | 82104 | CBldg 1321 Fairholme Boat Rental Shed | RMDM | Make minor repairs as needed and repaint the 3'x7' hollow metal exterior door every 5 years. | 1 | EA
Fairholme | 82109 | CParking AreaFairholme Store Paved | RMDM | Clean the parking lot and apply an emulsion sealer every 3 years. 7450 SF. | 7450 | SF
Fairholme | 82111 | Waterfront System Fairholm Store | CRDM | Replace the pile guide at the east end of the West to East Section of the floating dock, 1 EA | 1 | EA
Fairholme | 82111 | Waterfront System Fairholm Store | CRDM | Replace the 4' W x 20' L aluminum gangway with 4' high railing, 80SF | 80 | SF
Fairholme | 82111 | Waterfront System Fairholm Store | CRDM | Replace the 6' W x 60' L (three (3) 6' W x 20' L sections connected), West to East Section, HDPE floats with aluminum deck frame and a steel grate decking, 360 SF | 360 | SF
Fairholme | 82111 | Waterfront System Fairholm Store | CRDM | Replace the 6' W x 20' L, North to South Section, HDPE floats with aluminum deck frame and a steel grate decking, 120 SF | 120 | SF
Fairholme | 82111 | Waterfront System Fairholm Store | CRDM | Replace the 6" Diameter steel hollow pile at east end of West to East Section. This is not a structural pile, 30 LF | 1 | EA
Fairholme | 82111 | Waterfront System Fairholm Store | RMDM | Remove damaged vinyl fender and replace with in-kind vinyl fender, every 5 years. Assume 10% each occurrence. | 18 | EA
Fairholme | 82111 | Waterfront System Fairholm Store | RMDM | Replace the 4" high vinyl rub rail along the perimeter, except for at the west end on the West to East Section and the north end on the North to South Section, of both sections, 173 LF | 173 | EA
Fairholme | 82111 | Waterfront System Fairholm Store | RMDM | Replace the 4" high vinyl rub rail corner pieces, two (2) on each section, 4 EA | 4 | EA
Fairholme | 82111 | Waterfront System Fairholm Store | RMDM | Remove broken cleats and replace with in-kind cleats every 5 years. Assume 25% each occurrence. | 5 | EA
Lake Crescent | 82178 | CBldg 654 Lake Crescent Lodge | CRDM | Replace the cedar roof shingles within five years. | 9000 | SF
Lake Crescent | 82178 | CBldg 654 Lake Crescent Lodge | CRDM | Replace the 80 gallon electric water heater in the attic space near the offices at the end of its service life. | 1 | EA
Lake Crescent | 82178 | CBldg 654 Lake Crescent Lodge | CRDM | Replace the electrical branch wiring in the original lodge building at the end of its service life. 7298 SF. | 1 | EA
Lake Crescent | 82178 | CBldg 654 Lake Crescent Lodge | RMDM | Replace missing shingles (10%) and repaint the building. 5400 SF. | 5400 | SF
Lake Crescent | 82184 | CBldg 1362 Lake Crescent Lodge Triplex 10, 11 ,12 | RMDM | Sand and refinish 710sf of hardwood flooring. | 710 | SF
Lake Crescent | 82208 | CGrnd Lake Crescent Lodge Grounds | DM | Repair 60 square feet of damaged concrete sidewalk at the south stairwell to Storm King building. | 60 | SF
Lake Crescent | TBD-01 | LC Lodge Hotel Parking | RMDM | Clean parking lot and apply emulsion sealer every 3 years to extend service life. Repaint markings. 12075 SF | 12075 | SF
Lake Crescent | TBD-02 | LC Lodge Singer Parking | RMDM | Clean the parking lot, then apply an emulsion sealer every 3 years. Repaint markings. 11000 SF | 11000 | SF
Lake Crescent | TBD-03 | LC Lodge Memories Parking | RMDM | Clean parking lot and apply emulsion sealer every 3 years to extend service life. Repaint markings. 26900 SF | 26900 | SF
Lake Crescent | TBD-04 | LC Lodge Roosevelt Parking | RMDM | Clean the parking lot and apply an emulsion sealer every 3 years to extend its service life. 5190 SF. | 5190 | SF
Lake Crescent | TBD-05 | LC Lodge Service Area | RMDM | Clean the parking lot, then apply an emulsion sealer every 3 years. 5500 SF | 5500 | SF